## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-RT-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1082 |  |  | Transmital Date: 15-Jun-2022
Document Title: Electrical Network (Load Flow, Motor Starting & Short Circuit) Study Report |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1082 |  |  | Transmital Date: 15-Jun-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-RT-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 6 از 8 در نمایش حالت نرمال شبکه لازم است شبکه به صورت کامل با المانهای آن شامل: دیزل، کلیدهای محلی دیزل، کلید ورودی دیزل به MCC، و همچنین کلید رابط بین باس اضطراری و باس B و وضعیت هر کلید در حالت نرمال نمایش داده شود. |  | 1401-2294-172876 | 1401-05-20 | تمامی المانهای مورد نیاز شبکه به صورت کامل در مدار در نظر گرفته شدند. همچنین وضعیت کلیدها به صورت واقعی در شبکه مدل شدند.
2 | در نمایش حالت اضطراری مطابق با مدرک تک خطی تعداد کوپلر بین باس اضطراری و با س B به یک عدد کاهش داده شود. وضعیت NO یا NC بودن هر کلید در حالت اضطراری نماش داده شود. |  | 1401-2294-172876 | 1401-05-20
3 | سایر موارد متعاقبا ارسال خواهند شد. |  | 1401-2294-172876 | 1401-05-20 | در صورت وجود کامنتهای آتی، این مدرم به روزرسانی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 22-Jun-22 |  |  |  |  | Date: