## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0002-D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1632 |  |  | Transmital Date: 28-Nov-2022
Document Title: Electrical Typical Schematic Diagrams For LV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-EL-TR-1632 |  |  | Transmital Date: 28-Nov-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DG-0002-D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 13 از 16، پوش استاپ در مسیر سرویس اضافی می باشد. یک پوش استاپ Stay Put که در ابتدای مسیر قرار دارد کافی است. |  | 1401-2294-375922 | 1401-10-04 | اعمال گردید.
2 | برای حالت تست در مسیر استارت کنتاکت خودنگهدار در نظرگرفته شود. |  | 1401-2294-375922 | 1401-10-04 | در مسیر تست نیاز به کنتاکت خودنگهدار نمی باشد. چراکه این مسیر فقط برای تست عملکرد بوبین کنتاکتور اصلی مدار می باشد و با برداشتن شستی از روی آن باید به حالت قبل برگردد. در غیر این صورت باید یک استاپ نیز برای بازگردندان آن به وضعیت قبل از وصل در نظر گرفت که این امر نیاز نمی باشد.
3 | در حالت تست فقط یک عدد پوش استارت در نظر گرفته شود. پوش دوم حذف گردد. |  | 1401-2294-375922 | 1401-10-04 | اعمال گردید.
| سیگنال حالت ریموت نیز به اتاق کنترل ارسال گردد. مدرک I/O نیز بر همین اساس اصلاح گردد. |  | 1401-2294-375922 | 1401-10-04 | مطابق با مذاکرات انجام شده با آقای سعادتیان، مقرر گردید که فقط سیگنال حالت ریموت برای اتاق کنترل ارسال گردد. بر همین اساس مدرک IRP و I/O List ویرایش خواهد شد.
| مجموعه سویچ فیوز به عنوان یک بلوک واحد در مدرک نمایش داده شود. |  | 1401-2294-375922 | 1401-10-04 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Sadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 11-Dec-22 |  |  |  |  | Date: