## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0002-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date: 26/11/2022
Document Title: HVAC Calculation Note For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1441 |  |  | Transmital Date: 26/11/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0002-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | میزان بار گرمایی ناشی از تجهیزات الکتریکی (Heat Dissipation) برای فضاهای LV Room, HVRoom و Capacitor bank برچه اساسی انتخاب شده است. کاتالوگ‌ها و مستندات آن ارائه گردد. |  | 01/2294/325652 | 1401/09/02 | براساس اطلاعات موجود در پروژه های مشابه و با اعمال ضریب مناسب محاسبه شده است.
2 | در محاسبات تهویه اتاق باتری لحاظ نگردیده است. دمای اتاق نذکور باید 24درجه سانتیگراد باشد. |  | 01/2294/325652 | 1401/09/02 | براساس شرح کار و همچنین مبانی طراحی پروژه، کنترل دمای اتاق باتری نیاز نمیباشد.
3 | محاسبات کامل انتخاب هواکش برای اتاق باتری و اتاق CO2 ارائه شود. |  | 01/2294/325652 | 1401/09/02 | انجام شد.
4 | در جدول صفحه 23واحد دبی برای هردو فضا یکسان در نظر گرفته شود. همچنین مساحت و ارتفاع فضاها در جدول گنجانده شود. |  | 01/2294/325652 | 1401/09/02 | انجام شد.
5 | مطابق اسناد پیمان (PROCESS MAIN EQUIPMENT LIST -1560-BK-NCS-ME--LIST-0006-00) میبایست جهت فضاهای موجود و توسعه ای یک دستگاه HVAC یکپارچه در نظر گرفته شود. |  | 01/2294/325652 | 1401/09/02 | مطابق با شرح کار صفحه 37 از 153 پیوست 10 مربوط به شرح کار ایستگاه تقویت فشار( برای ساختمان توسعه ای Substation بایستی سیستم HVAC با در نظرگرفتن تغییرات ابعادی و تجهیزاتی، طراحی مجدد گردیده و کلیه تمهیدات مورد نیاز برای سیستم تهویه مطبوع فضاها ی توسعه یافته اضافه گردد.) مطابق بند فوق طراحی برای کل ساختمان انجام شد و طبق آن سیستم موجود جوابگوی بار قبلی ساختمان بوده و برای تهویه مطبوع فضاهای توسعه یافته اسپلیت با ظرفیت های مشخص شده در مدرک محاسبات در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature
| Date: |  |  |  |  | Date:21/01/2023