## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0003_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1509 |  |  | Transmital Date: 18-Oct-2022
Document Title: Single Line Diagram For LV Power Distribution Panel of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1509 |  |  | Transmital Date: 18-Oct-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-SL-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 4 از ریپلای شیت: در خصوص ضرورت نصب کولر مطابق با بند 1-2-2-10 شرح کار برقرسانی به تلمبه های درون چاهی نصب یک دستگاه کولر اسپلیت در تعهد پیمانکار پروژه می باشد و از آنجا که اتاق باتری جزو ناحیه خطر محسوب می شود، لذا کولر آن نیز می بایست متناسب با ناحیه خطر تهیه گردد. |  | 1401-2294-325657 | 1401-09-02 | مطابق با محاسبات سیستم HVAC، نیاز به در نظر گرفتن کولر اسپلیت برای اتاق باتری نمی باشد. لذا فیدر مجزا در نظر گرفته نشده است.
2 | صفحه 4 از 4: تعداد فیدرهای خروجی و توان هر فیدر می بایست پس از تعیین تکلیف سیستم روشنایی محوطه سرچاهی به روزرسانی شود. |  | 1401-2294-325657 | 1401-09-02 | مطابق با آخرین مدرک محاسبات و جانمایی روشنایی اتاق نگهبانی و سوییچگیر که به ترتیب با ترنسمیتالهای 1754 و 1749 ارسال شده است، این مدرک ویرایش گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Oct-22 |  |  |  |  | Date: