## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0003_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1509 |  |  | Transmital Date: 18-Oct-2022
Document Title: Single Line Diagram For LV Power Distribution Panel of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0107-EL-TR-1509 |  |  | Transmital Date: 18-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-SL-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This documents shall be revised and issued as IFA after finalizing or minor comments on lighting and small power layout. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | این مدرک مطابق با آخرین ویرایش مدرک جانمایی روشنایی اصلاح گردید و در صورت هر گونه تغییر، مدارک ویرایش خواهد شد. |  |  | Noted and Closed.
2 | According to NO. of outdoor area lighting panel feeders, It is recommended to area lighting feeders be supplied from security building lighting panel. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | به علت گستردگی سایت و فاصله از ساختمان نگهبانی تا پایه های روشنایی، تابلو WELL XX-DP03 تغذیه شونده از سوئیچگیر به صورت مجزا در نظر گرفته شده است. |  |  | See below item 9.
3 | Lighting layouts for buidlings and outdoor area shall be added as reference document. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید. |  |  | Noted and Closed.
4 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23
4-1 | Considered seperat sub-bus for outdoor wallmounted lighting feeder in single line diagram shall be deleted. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | حذف گردید. |  |  | Noted and Closed.
4-2 | Installation type of lighting panels (Surface/Flush mounted) shall be specified in table. (Note 1 shall be modified base on installation type.) |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید. |  |  | Noted and Closed.
5 | Security building SLD: Type of CB. for feeder 7 shall be modified. (shall be considered RCBO instead of MCB) |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید. |  |  | Noted and Closed.
6 | Security building SLD: MCB technical description for feeders NO. 7&9 shall be added on SLD. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید. |  |  | Noted and Closed.
7 | Outgoing cables form switchgear building lighting panel to diesel generator shelter shall be armour type. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | با توجه به این موضوع که مکان دیزل ژنراتور نهایی نشده است در صورتیکه کابل روشنایی آن زیرزمینی باشد، از کابل آرموردار استفاده خواهد شد. لازم به ذکر است در ویرایش های بعدی معماری آن تکمیل و در این مدرک روشنایی آن نمایش داده خواهد شد. |  |  | Will be checked later.
8 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | در صورت وجود کامنت احتمالی متعاقبا بررسی خواهد شد. |  |  | Noted and Closed.
9 | See above item 2: According to NO. of outdoor area lighting panel feeders and telephone conversation, It is recommended to area lighting feeders be supplied from switchgear building lighting panel. |  | BK-SUR-ENG-ELE-01-06039 | 2022-10-31 | اعمال گردید.
10 | Spare RCBO feeder range shall be modified to 25A instead of 16A for switchgear/Security building LP. |  | BK-SUR-ENG-ELE-01-06039 | 2022-10-31 | اعمال گردید.
11 | According to meeting date 1401.08.04, it is necessary to considered a separate feeder for IRP panel with rating capacity 1KW in switchgear LP. |  | BK-SUR-ENG-ELE-01-06039 | 2022-10-31 | یک فیدر یک کیلووات برای روشنایی و هیتر و فن تابلوی IRP در نظر گرفته شده است.
12 | Cable size for socket feeders in switchgear LP SLD shall be modified to 3x4 CU/PVC/PVC instead of 3X2.5 CU/PVC/PVC. |  | BK-SUR-ENG-ELE-01-06039 | 2022-10-31 | اعمال گردید.
13 | Incoming cable size in SLD and table are different from each other for switchgear building LP, it shall be rechecked and modified. Meanwhile it shall be clarify why the incoming cable of switchgear LP is 4 core but security building is 5 core. |  | BK-SUR-ENG-ELE-01-06039 | 2022-10-31 | اصلاح صورت پذیرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Oct-22 |  |  |  |  | Date: