## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-ME-DT-0001_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1469 |  |  | Transmital Date: 09/Oct/2022
Document Title: Mechanical Data Sheets For Oil Sump Pump (P-1701) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0109-ME-TR-1469 |  |  | Transmital Date: 09/Oct/2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-ME-DT-0001_D03 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به تغییر نوع پمپ نسبت به اسناد پایه بررسی این مدرک پس از ارائه دلایل مربوطه و اخذ تاییدیه کمیته تغییرات امکان پذیر خواهد بود. |  | 01/2294/367289 | 1401/09/29 | همانطور که پیش تر در پاسخ به نامه کارفرمای محترم به شماره 01/2294/229741 اعلام گردید، پمپ مذکور وظیفه تخلیه مایعات و آلودگی های جمع شده به علت تعمیر و تخلیه تجهیزات را دارد. مطابق با مدارک پایه و اسناد مناقصه ، این پمپ از نوع افقی بود ولی برای رفع مشکل NPSHاحتمالی در صورت گرفتگی foot valve ، این پیمانکار پیشنهاد تغییر نوع آن به پمپ عمودی را داد تا احتمال وقوع کاویتاسیون بواسطه نبود NPSH مورد نیاز برای پمپ های افقی کاهش یابد. با توجه به هد و دبی موجود و همچنین استعلام از سازندگان، پمپ عمودی از نوع VS1 پیشنهاد گردیده. لازم به ذکر است که درخواست تغییر(Change Order) این پمپ نسبت به اسناد پایه در اسرع وقت برای کارفرمای محترم ارسال خواهد گردید لذا خواهشمند است بررسی این مدرک در دستور کار آن کارفرمای محترم قرار گیرد.
2 | - |  | - | - | -تغییرات ولتاژ و فرکانس مطابق آخرین ویرایش مدرک Electrical design criteria اصلاح گردید. -نوت های شماره 13 و 32 مطابق نقطه نظرات شرکت پتروایران اصلاح گردید. -مطابق آخرین محاسبات هیدرولیکی پمپ oil sump ، اطلاعات فرآیندی اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: |  |  |  |  | Date: 01/24/2023