## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-W046S-PEDCO-110-SA-PY-0001_D00 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-1003 |  |  | Transmital Date:25/MAY/2022
Document Title: Hazardous Area Classification Layout - W046S |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-1003 |  |  | Transmital Date:25/MAY/2022
[5 empty] | CRS No: NISOC-CRS-BK-W046S-PEDCO-110-SA-PY-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | طبقه بندی منطقه خطر مربوط به سرچاه بر اساس مدرک Hazard Source List وشکل استاندارد اصلاح شود . |  | 1401-2294-113875 | 1401/04/02 | اصلاح گردید.
2 | طبقه بندی منطقه خطر مربوط به Fucl Tank بر اساس مدرک Hazard Source List در نقشه نمایش داده شود . |  | 1401-2294-113875 | 1401/04/02 | اعمال گردید.
3 | طبقه بندی منطقه خطر مربوط به Flange ,Valve و... بر اساس مدرک Hazard Source List در قسمت Notes ذکر گردد. |  | 1401-2294-113875 | 1401/04/02 | طبقه بندی منطقه خطر مربوط به Flange ,Valve درقسمت Notes اضافه شد.
4 | با توجه به وجود بخارات گاز هیدروژن در اتاق باتری کلید خانه ، می بایست در مدرک ناحیه Hazard جهت این اتاق و محدوده درب اتاق باتری و فن هواکش نمایش داده شود. |  | 1401-2294-113875 | 1401/04/02 | طبقه بندی منطقه خطر مربوط به اتاق باتری درقسمت Notes اضافه شد. تجهیزات اشاره شده در نقشه معماری مربوطه دیده شده است.
5 | نمای جانبی طبقه بندی منطقه خطر کلیه تجهیزات بر اساس اشکال استاندارد به مدرک اضافه شود |  | 1401-2294-113875 | 1401/04/02 | اعمال گردید.
6 | ویرایش جدید مدرک با وضوح بیشتری جهت بررسی به این امور ارسال گردد. |  | 1401-2294-113875 | 1401/04/02 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: