## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W046S-PEDCO-110-HV-CN-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date:11/26/2022
Document Title:HVAC Calculation Note For Switchgear Building - W046S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-1441 |  |  | Transmital Date:11/26/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W046S-PEDCO-110-HV-CN-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
3 | to explain reason why for roof and external walls insulation has not considered. |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-01 | Wall Insulation has replaced with rock wool with 50 mm thickness and R: 1.19 m2.K/W and Roof Insulation has replaced with Polystyren block with 200mm thickness according to roof detail in calculation document(roof detail has taken from civil and structure department and will be specified in architecture drawings next rev. ).
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.naserizadeh |  |  | Clarified By: H. Adineh | Signature
| Date: 10/01/2022 |  |  |  |  | Date: 24/01/2023