## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-PY-0005_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1410 |  |  | Transmital Date: 18 Sep 2022
Document Title: F&G Location Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1410 |  |  | Transmital Date: 18 Sep 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-PY-0005_D01 |  |  | Comment Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است با توجه به ابعاد اتاق کنترل، یک دتکتور دودیاب اضافه شود. |  | 01/2294/279720 | 1401/08/03 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
2 | با توجه به تغییر کاربردی اتاق باطری به انبار، لازم است یک دتکتور دودیاب در اتاق نصب شود. |  | 01/2294/279720 | 1401/08/03 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
3 | در نقشه اتاق باطری ، MAC2202 به بیرون اتاق انتقال داده شود. |  | 01/2294/279720 | 1401/08/03 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
4 | در نقشه ساختمان برق، MAC-2302 به بیرون اتاق انتقال داده شود. |  | 01/2294/279720 | 1401/08/03 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
5 | لازم است در ساختمان هایی که دتکتور گاز هیدروژن وجود دارد آلارم دیداری زرد رنگ در کنار آلارم دیداری قرمز رنگ نیز لحاظ شود. |  | 01/2294/279720 | 1401/08/03 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
6 | جهت کارایی بیشتر، مقتضی است سنسورهای دود در بالای مرکز تابلوهای MV&LV و تابلوی بانک های خازنی در ساختمان کلیدخانه جانمایی گردند. |  | 01/2294/279720 | 1401/08/03 | مدرک اصلاح گردید و جانمایی سنسورهای دودیاب درساختمان کلیدخانه بصورتی جانمایی گردید که کل ساختمان را پوشش دهند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 3 Oct 2022 |  |  |  |  | Date: