## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-SA-PY-0005-D00 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-T-0923 |  |  | Transmital Date:10/MAY/2022
Document Title: Escape Route & Safety Sign Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-T-0923 |  |  | Transmital Date:10/MAY/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-SA-PY-0005-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است تابلو های خطر آزاد شدن گاز،خطر آزاد شدن گاز H2S ،مسیر های خروج اضطراری ،ضرورت استفاده از تجهیزات حفاظت فردی ،منع برافروختن آتش و استعمال دخانیات ،درب خروج اضطراری ،خطر سقوط در گودال ،محدودیت سرعت و ...به تعداد کافی در سایت جانمایی شود . |  | 1401-2294-94639 | 1401/03/20 | اعمال گردید.
2 | در نقاطی که نمونه گیری انجام می پذیرد تابلویی که محتوای آن دستورالعمل نمونه گیری ،MSDS سیال و نوع وسایل حفاظت فردی در زمان نمونه گیری می باشد نصب گردد. |  | 1401-2294-94639 | 1401/03/20 | اعمال گردید.
3 | در سایبان نگهداری مواد شیمیایی و سایبان های پکیج مواد شیمیایی بایستی تابلویی که محتوای آن لوزی خطر ، ماده مورد نیاز جهت اطفای حریق ،خطرات بهداشتی و کمک های اولیه و...می باشد نصب گردد. |  | 1401-2294-94639 | 1401/03/20 | اعمال گردید.
4 | لازم است پس از نهایی شدن جانمایی تجهییزات ایمنی و آتش نشانی و سیستم F&G ، مدرک فوق جهت بررسی به این امور ارسال گردد. |  | 1401-2294-94639 | 1401/03/20 | مدرک ، بر اساس آخرین ویرایش مدرک F&G layout تولید شده در بخش ابزار دقیق تهیه و ارائه گردیده است .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: