## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W046S-PEDCO-110-HV-PY-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date: 11/26/2022
Document Title:HVAC System Layout For Switchgear Building - W046S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-1441 |  |  | Transmital Date: 11/26/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W046S-PEDCO-110-HV-PY-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
2 | indoor temperature for battery room shall condition (T=250C) this has mentioned in NIOEC SP-1 and ASHRAE handbook pages also in our comments for design criteria (see attachments) |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-02 | According to Basics of Project Design, temperature control of Battery room is not needed.
3 | exhaust fan for battery room shall be had 100 % redundancy unit (it means that , two exhaust fan unit shall consider) this is same as requirements for battery room in control building according to document number BK-GNRAL-PEDCO-000-HV-DC-0001_D01, also as it is mentioned in NIOEC SP-1 and ASHRAE handbook pages (see attachments) |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-01 | It has not been specified in Project Contract.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.naserizadeh |  |  | Clarified By: H. Adineh | Signature
| Date: 10/01/2022 |  |  |  |  | Date: 31/01/2023