## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DG-0010_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1412 |  |  | Transmital Date: 19 Sep 2022
Document Title: F&G Cause and Effect Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1412 |  |  | Transmital Date: 19 Sep 2022
[5 empty] | CRS No: NISOC-CRS- BK-W007S-PEDCO-110-IN-DG-0010_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Effect مربوط به مشخص شدن آدرس بر روی پنل و فعال شدن آلارم پنل فعال گردد. |  | 1401-2294-296399 | 1401/08/14 | مطابق نظر کارفرمای محترم اصلاح گردید.
2 | در حالت LEL 5% گاز هیدروژن ، فن استارت شود. |  | 1401-2294-296399 | 1401/08/14 | مطابق نظر کارفرمای محترم اصلاح گردید.
3 | در حالت LEL % 10 گاز هیدروژن ، Battery charger shut down فعال شود. |  | 1401-2294-296399 | 1401/08/14 | مطابق نظر کارفرمای محترم اصلاح گردید.
4 | لازم است مدرک بر اساس نقطه نظرات این امور در خصوص نقشه های جانمایی اصلاح شود. |  | 1401-2294-296399 | 1401/08/14 | مطابق آخرین نسخه از مدرک نقشه های جانمایی، اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: