## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1282 |  |  | Transmital Date: 17 Aug 2022
Document Title: I/O List For F&G Systems - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1282 |  |  | Transmital Date: 17 Aug 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-LI-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05549 | 2022-08-28 | نظر کارفرمای محترم ، ملاحظه گردیده شد.
2 | با توجه به اينكه مدرك F&G Location Layout نهايي نيست و داراي كامنت با كد 3 مي باشد.(مانند در نظر گرفتن Voting براي H2 Detector ها) موارد بعد از تغيير در اين مدرك نيز منعكس شود. |  | BK-SUR-ENG-INS-01-05549 | 2022-08-28 | مطابق آخرین نسخه از مدرک نقشه های جانمایی، اصلاح گردید.
3 | با توجه به نقطه نظر كارفرما مبني بر گذاشتن ادوات F&G بر روي تمامي ساختمان هاي موجود، موارد پيگيري و نهايي گردد. |  | BK-SUR-ENG-INS-01-05549 | 2022-08-28 | مطابق نظر کارفرمای محترم اصلاح گردید.
4 | با توجه به سيگنال هاي ارائه شده، لطفا در نظر گرفته شود كه FACP هم بصورت Addressable و هم Convential باشد. |  | BK-SUR-ENG-INS-01-05549 | 2022-08-28 | با توجه به اینکه در این سایت هیچ دستور ESD به وسیله سیستم FACP ارسال نمی گردد ، نیاز به در نظر گرفتن این پنل به صورت CONVENTIONAL نمی باشد. لازم به ذکر است با دریافت سیگنال از HGDها(%LEL 10)تنها دستور ایزوله کردن باتری ها و جلوگیری از شارژ شدن ها به سیستم ارسال میگردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 28 Aug 2022 |  |  |  |  | Date: