## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 11
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0003 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR ESD SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | DEC.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number:'F0Z-708969
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 11
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X |  | X |  |  |  | 69
6 | X | X | X |  | X |  |  |  | 70
7 | X | X | X |  | X |  |  |  | 71
8 | X | X | X |  | X |  |  |  | 72
9 |  | X | X |  | X |  |  |  | 73
10 |  | X | X |  | X |  |  |  | 74
11 |  |  | X |  | X |  |  |  | 75
12 |  |  | X | [5 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 11
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0003 | D02
REFERENCES:
|  | Symbol & Legend For PFD and P&ID | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D02
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D04
|  | P&ID - Slug Catcher System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D04
|  | P&ID - Gas Compression Inlet Knock Out Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D04
|  | P&ID - 1st Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D04
|  | P&ID - 1st Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D04
|  | P&ID - 1st Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D04
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D04
|  | P&ID - 2nd Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D04
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D04
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D04
|  | P&ID - Gas Compression Dehydration Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D04
|  | P&ID - Lean Glycol Storage Tank | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D04
|  | P&ID - Instrument & Plant Air System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D04
|  | P&ID - Nitrogen Generation System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D04
|  | P&ID - Close Drain System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D04
|  | P&ID - Corrosion Inhibitor Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D04
|  | P&ID - Methanol Injection Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D04
|  | P&ID - LP Flare System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D04
|  | P&ID - Oily Water Sewer | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D04
|  | P&ID - Fuel Gas System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D04
|  | P&ID - Diesel Oil System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D04
|  | P&ID - Potable Water System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D04
|  | P&ID - Glycol Sump Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D04
|  | P&ID - Fire Water Network | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D01
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D03
|  | Data Sheets For ESD Console/F&G Matrix Panel | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017_D00
|  | ESD Level Hierarchy | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003_D00
NOTES:
| NOTE 1 : |  | ALL OF ANALOGE TRANSMITTER SHALL BE CONSIDERED INTRINSICALLY SAFE (EEXIA) & ALL OF DIGITAL TRANSMITTER ARE NON INTRINSICALLY SAFE (EEXD).
| NOTE 2 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
| NOTE 3 : |  | ESD EQUIPMENT & ALL OF EQUIPMENT THAT IS ASSIGNED IN A CONTROL LOOP, ARE REDUNDANT.
| NOTE 4 : |  | ALL I/Os REQUIRED FOR DEHYDRATION PACKAGE (PK-2101) WILL BE ADDED TO THIS SUMMARY AS PER VENDOR DATA LATER.
| NOTE 5 : |  | ALL I/Os REQUIRED FOR ESD SHALL BE SHOWN IN DCS BY SERIAL LINK.

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 11
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 | D02
ESD I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 59 |  | 72 | NOTES 1,2,3,4 | 70.8
| 2 |  | AI-IS-NR |  | IS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 3 |  | AO-IS-R |  | IS | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 4 |  | AO-IS-NR |  | IS | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 5 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 38 |  | 46 | NOTES 1,2,3,4 | 45.6
| 6 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 7 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 89 |  | 107 | NOTES 1,2,3,4 | 106.8
| 8 |  | DO-NIS-NR |  | NIS | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
Estimated I/Os ( 30 No.) for Dehydration package to be considered in addition to above summary (Note4)
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
D03

## IO List for ESD System
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0003 |  |  | D02
I/O List For ESD System
ITEM | ESD LEVEL | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[15 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | 1 | ESOV-2101 | Solenoid Valve | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
2 | 1 | ESOV-2102 | Solenoid Valve | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
3 | 1 | PIT-2111 | Pressure Indicator Transmitter | From Gas Pig Receiver (PR-2102) |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
4 | 1 , 3 | LIT-2112 | Level Indicator Transmitter | SLUG CATCHER DRUM (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
5 | 3 | PIT-2115 | Pressure Indicator Transmitter | FROM P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
6 | 3 | PIT-2114A | Pressure Indicator Transmitter | TO P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
7 | 3 | PIT-2114B | Pressure Indicator Transmitter | TO P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
8 | 3 | PIT-2116A | Pressure Indicator Transmitter | CDH-112-0012-CN05-3"-PT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
9 | 3 | PIT-2116B | Pressure Indicator Transmitter | CDH-112-0013-CN05-3"-PT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
10 | 3 | ESD-P-2111-A | Trip Command | SLUG PUMP (P-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
11 | 3 | ESD-P-2111-B | Trip Command | SLUG PUMP (P-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
12 | 3 | ESOV-2112 | Solenoid Valve | FROM P-2101A/B TO BINAK PRODUCTION UNIT (After Slug Pumps) |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
13 | 3 | ESOV-2113 | Solenoid Valve | From V-2105 /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
14 | 1 | LIT-2117 | Level Indicator Transmitter | INLET KNOCK OUT DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
15 | 3 | LIT-2118 | Level Indicator Transmitter | INLET KNOCK OUT DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
16 | 1 | PIT-2116 | Pressure Indicator Transmitter | FROM SLUG CATCHER DRUM (V-2104) To V-2105 |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
17 | 2 | ESOV-2121A | Solenoid Valve | From 1ST Stage Gas Compression Suction Manifold To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
18 | 2 , 3 | LIT-2122A | Level Indicator Transmitter | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #A (V-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
19 | 3 | ESOV-2122A | Solenoid Valve | From V-2101-ATo Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
20 | 2 | ESOV-2121B | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
21 | 2 , 3 | LIT-2122B | Level Indicator Transmitter | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #B (V-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
22 | 3 | ESOV-2122B | Solenoid Valve | From V-2101-BTo Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
23 | 2 | ESOV-2121C | Solenoid Valve | From 1ST Stage Gas Compression Suction Manifold To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
24 | 2 , 3 | LIT-2122C | Level Indicator Transmitter | 1ST STAGE GAS COMPRESSION SUCTION DRUM TRAIN #C (V-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
25 | 3 | ESOV-2122C | Solenoid Valve | To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
26 | 2 | PIT-2122A | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101A) To C-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
27 | 2 | PIT-2125A | Pressure Indicator Transmitter | Outlet Comp. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
28 | 2 | TIT-2124A | Temperature Indicator Transmitter | Outlet Comp. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
29 | 2A | ESDR2A-C-2101-A | Trip Command With Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
30 | 2 | ESDR2-C-2101-A | Trip Command Without Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
31 | 2A | ESD2A-C-2101-A | Trip Alarm With Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
32 | 2 | ESD2-C-2101-A | Trip Alarm Without Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
33 | 2A | ESOV-2122A | Solenoid Valve | 1ST Stage Gas Compressor (C-2101-A) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
34 | 2 | PIT-2122B | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101B) To C-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D03 MODIFIED
35 | 2 | PIT-2125B | Pressure Indicator Transmitter | Outlet Comp. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
36 | 2 | TIT-2124B | Temperature Indicator Transmitter | Outlet Comp. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
37 | 2A | ESDR2A-C-2101-B | Trip Command With Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
38 | 2 | ESDR2-C-2101-B | Trip Command Without Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
39 | 2A | ESD2A-C-2101-B | Trip Alarm With Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
40 | 2 | ESD2-C-2101-B | Trip Alarm Without Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
41 | 2A | ESOV-2122B | Solenoid Valve | 1ST Stage Gas Compressor (C-2101-B) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
42 | 2 | PIT-2122C | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101C) To C-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X | X |  | X |  |  | D03 MODIFIED
43 | 2 | PIT-2125C | Pressure Indicator Transmitter | Outlet Comp. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
44 | 2 | TIT-2124C | Temperature Indicator Transmitter | Outlet Comp. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
45 | 2A | ESDR2A-C-2101-C | Trip Command With Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
46 | 2 | ESDR2-C-2101-C | Trip Command Without Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
47 | 2A | ESD2A-C-2101-C | Trip Alarm With Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
48 | 2 | ESD2-C-2101-C | Trip Alarm Without Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
49 | 2A | ESOV-2122C | Solenoid Valve | 1ST Stage Gas Compressor (C-2101-C) Bypass Valve |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
50 | 3 | VSHH-2121A | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
51 | 3 | VSHH-2122A | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
52 | 3 | ESD-AE-2101-A-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
53 | 3 | ESD-AE-2101-A-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
54 | 2 | TIT-2125A | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
55 | 3 | VSHH-2121B | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
56 | 3 | VSHH-2122B | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
57 | 3 | ESD-AE-2101-B-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
58 | 3 | ESD-AE-2101-B-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
59 | 2 | TIT-2125B | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
60 | 3 | VSHH-2121C | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
61 | 3 | VSHH-2122C | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
62 | 3 | ESD-AE-2101-C-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
63 | 3 | ESD-AE-2101-C-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
64 | 2 | TIT-2125C | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
65 | 2 , 3 | LIT-2132A | Level Indicator Transmitter | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A (V-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 MODIFIED
66 | 2A | BSOV-2134A | Solenoid Valve | From V-2102-A To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
67 | 3 | ESOV-2131A | Solenoid Valve | From V-2102-A To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
68 | 2 , 3 | LIT-2132B | Level Indicator Transmitter | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A (V-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 MODIFIED
69 | 2A | BSOV-2134B | Solenoid Valve | From V-2102-B To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
70 | 3 | ESOV-2131B | Solenoid Valve | From V-2102-B To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
71 | 2 , 3 | LIT-2132C | Level Indicator Transmitter | 2ND STAGE GAS COMPRESSOR SUCTION DRUM TRAIN #A (V-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X | X |  | X | X |  |  | D03 MODIFIED
72 | 2A | BSOV-2134C | Solenoid Valve | From V-2102-C To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
73 | 3 | ESOV-2131C | Solenoid Valve | From V-2102-C To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
74 | 2 | PIT-2131A | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102A) To C-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
75 | 2 | PIT-2134A | Pressure Indicator Transmitter | from V-2102A To 2ND Stage Air Cooler (AE-2102A) |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
76 | 2 | TIT-2134A | Temperature Indicator Transmitter | from V-2102A To 2ND Stage Air Cooler (AE-2102A) |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
77 | 2 | PIT-2131B | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102B) To C-2102-B |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
78 | 2 | PIT-2134B | Pressure Indicator Transmitter | from V-2102B To 2ND Stage Air Cooler (AE-2102B) |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
79 | 2 | TIT-2134B | Temperature Indicator Transmitter | from V-2102B To 2ND Stage Air Cooler (AE-2102B) |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
80 | 2 | PIT-2131C | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102C) To C-2102-C |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
81 | 2 | PIT-2134C | Pressure Indicator Transmitter | from V-2102C To 2ND Stage Air Cooler (AE-2102C) |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
82 | 2 | TIT-2134C | Temperature Indicator Transmitter | from V-2102C To 2ND Stage Air Cooler (AE-2102C) |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
83 | 3 | ESD-AE-2102-A-1 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
84 | 3 | ESD-AE-2102-A-2 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
85 | 3 | VSHH-2131A | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
86 | 3 | VSHH-2132A | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
87 | 2 | TIT-2136A | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
88 | 2A | BSOV-2132A | Solenoid Valve | From AE-2102-A To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
89 | 2 | ESOV-2133A | Solenoid Valve | From AE-2102-A To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
90 | 3 | ESD-AE-2102-B-1 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
91 | 3 | ESD-AE-2102-B-2 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
92 | 3 | VSHH-2131B | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
93 | 3 | VSHH-2132B | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
94 | 2 | TIT-2136B | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X |  |  | X |  |  | D03 MODIFIED
95 | 2A | BSOV-2132B | Solenoid Valve | From AE-2102-B To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
96 | 2 | ESOV-2133B | Solenoid Valve | From AE-2102-B To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
97 | 3 | ESD-AE-2102-C-1 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
98 | 3 | ESD-AE-2102-C-2 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
99 | 3 | ESD-AE-2102-C-1 | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
100 | 3 | ESD-AE-2102-C-2 | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
101 | 2 | TIT-2136C | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X |  |  | X |  |  | D03 MODIFIED
102 | 2A | BSOV-2132C | Solenoid Valve | From AE-2102-C To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
103 | 2 | ESOV-2133C | Solenoid Valve | From AE-2102-B To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
104 | 1A | BSOV-2141 | Solenoid Valve | FROM METHANOL HEADER To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
105 | 1 | ESOV-2142 | Solenoid Valve | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
106 | 1 | ESOV-2143 | Solenoid Valve | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
107 | 1 , 3 | LIT-2142 | Level Indicator Transmitter | GAS COMPRESSION DISCHARGE DRUM (V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
108 | 3 | ESOV-2144 | Solenoid Valve | From V-2103 To TO CLOSED DRAIN HEADER |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
109 | 1A | BSOV-2151 | Solenoid Valve | DEHYDRATION PACKAGE (PK-2101)To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
110 | 3 | LIT-2161 | Level Indicator Transmitter | LEAN GLYCOL STORAGE TANK (TK-2102) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
111 | 3 | ESD-P-2161-A | Trip Command | GLYCOL TRANSFER PUMP (P-2103A) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
112 | 3 | ESD-P-2161-B | Trip Command | GLYCOL TRANSFER PUMP (P-2103B) |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
113 | 3 | PIT-2202 | Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
114 | 3 | ESOV-2201 | Solenoid Valve | INSTRUMENT & PLANT AIR SYSTEM HEADER (PK-C-2203A/B , PK-DR-2203A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
115 | 3 | ESD-PK-C-2203 A | Trip Command | Air Compressor Package (PK-C-2203 A) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
116 | 3 | ESD-PK-C-2203 B | Trip Command | Air Compressor Package (PK-C-2203 B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
117 | 1A | PT-2201A | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
118 | 1A | PT-2201B | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
119 | 1A | PT-2201C | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
120 | 1 | PIT-2211 | Pressure Indicator Transmitter | NIT-112-0024-AN01-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0016 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
121 | 3 | PIT-2222A | Pressure Indicator Transmitter | CDH-112-0032-AN07-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
122 | 3 | PIT-2222B | Pressure Indicator Transmitter | CDH-112-0033-AN07-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
123 | 3 | ESD-P-2221-A | Trip Command | CLOSED DRAIN DRUM PUMP (P-2202-A) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
124 | 3 | ESD-P-2221-B | Trip Command | CLOSED DRAIN DRUM PUMP (P-2202-B) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
125 | 1A | ESD-P-2222-A | Trip Command | SUMP PUMP (P-2203-A) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
126 | 1A | ESD-P-2222-B | Trip Command | SUMP PUMP (P-2203-B) |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
127 | 1 | ESD-PK-2207 | Trip Command | Corrosion Inhibitor Package (PK-TK-2207)/CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 |  |  | DO-NIS-R |  | ESD |  | PK-2207 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
128 | 3 | ESD-P-2251A | Trip Command | LP Flare K.O. Drum Pump (P-2201 A) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
129 | 3 | ESD-P-2251B | Trip Command | LP Flare K.O. Drum Pump (P-2201 B) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
130 | 1 | LIT-2252A | Level Indicator Transmitter | LP FLARE K.O. DRUM (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
131 | 1 | LIT-2252B | Level Indicator Transmitter | LP FLARE K.O. DRUM (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
132 | 1 | LIT-2252C | Level Indicator Transmitter | LP FLARE K.O. DRUM (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X |  |  | D03 MODIFIED
133 | 3 | PIT-2251A | Pressure Indicator Transmitter | LP FLARE K.O. DRUM PUMP (P-2201 A) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
134 | 3 | PIT-2251B | Pressure Indicator Transmitter | LP FLARE K.O. DRUM PUMP (P-2201 B) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
135 | 3 | LIT-2253 | Level Indicator Transmitter | LP FLARE K.O. DRUM (V-2201) |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
136 | 1A | ESD-PK-2281 | Trip Command | LP FLARE STACK PACKAGE (Air Blower) |  | BK-GCS-PEDCO-120-PR-PI-0020 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
137 | 3 | ESOV-2272 | Solenoid Valve | From Inlet K.O. Drum (V-2105) To V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
138 | 3 | LIT-2272 | Level Indicator Transmitter | FUEL GAS K.O. DRUM (V-2205) |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D03 MODIFIED
139 | 3 | ESOV-2271 | Solenoid Valve | From Inlet K.O. Drum (V-2105) To TO CLOSED DRAIN HEADER |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
140 | 1A | ESD-P-2293 | Trip Command | GLYCOL DRAIN PUMP (P-2104) |  | BK-GCS-PEDCO-120-PR-PI-0025 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
141 | 1 | ESOV-3101 | Solenoid Valve | PIPELINE: From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
142 | 1 | PIT-3201A | Pressure Indicator Transmitter | PIPELINE: From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
143 | 1 | PIT-3201B | Pressure Indicator Transmitter | PIPELINE: From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
144 | 1 | PIT-3201C | Pressure Indicator Transmitter | PIPELINE: From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D03 MODIFIED
145 | 0 | ESD0-UPS-CH1 | 110V AC UPS, CH01 FAULT STATUS | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | ELECTRICAL (UPS CHARGER) |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
146 | 0 | ESD0-UPS-CH2 | 110V AC UPS, CH02 FAULT STATUS | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | ELECTRICAL (UPS CHARGER) |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 ADDED
147 | 0 | ESDR 0-F&G | CONFIRMED FLAMMABLE GAS IN HVAC INTAKE (COMMAND FROM F&G) | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
148 | 0 | ESD 0-EL1A | 11/0.4 KV SWGR-Transformer Feeder-Q2 (EMERGENCY + NORMAL POWER ISOLATION) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL MV SWG (IRP) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
149 | 0 | ESD 0-EL1B | 11/0.4 KV SWGR-Transformer Feeder-Q2 (EMERGENCY + NORMAL POWER ISOLATION) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL MV SWG (IRP) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
150 | 0 | ESD 0-EL2A | 110V AC UPS, CH01 ISOLATION COMMAND | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (UPS CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
151 | 0 | ESD 0-EL2B | 110V AC UPS, CH02 ISOLATION COMMAND | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (UPS CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
152 | 1A | ESDR 1A-F&G | CONFIRMED FLAMMABLE/ TOXIC GAS IN PROCESS AREA (COMMAND FROM F&G) | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
153 | 1A | ESD 1A-EL1 | POWER ISOLATION IN PROCESS AREA | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 DELETED
154 | 1 | ESDR 1-EL1 | NETWORK POWER FAILURE SWITCH ACTIVATION | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | IRP |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
155 | 1 | ESDR 1-DC | DC CHARGER FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | UPS CHARGER |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
156 | 1 | ESDR 1-PCS | PCS FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
157 | 1 | ESDR 1-FLR | FLARE IGNITION FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
158 | 1A | ESD 1A-F&G | CONFIRMED FIRE IN FIRE ZONE (PROCESS) AREA (COMMAND FROM F&G) | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
159 | 0 | ESD0-LAMP | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
160 | 1A | ESD1A-LAMP | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
161 | 2A | ESD2A-A-LAMP | TRAIN A SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
162 | 2A | ESD2A-B-LAMP | TRAIN B SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
163 | 2A | ESD2A-C-LAMP | TRAIN C SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
164 | --- | LAMP-ESD-INH | ESD INHIBIT LAMP | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
165 | --- | LAMP-ESD-RST | ESD RESET LAMP | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
166 | 1 | ESD1-LAMP | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
167 | 2 | ESD2-A-LAMP | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
168 | 2 | ESD2-B-LAMP | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
169 | 2 | ESD2-C-LAMP | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 MODIFIED
170 | 3 | ESD 3-A-LAMP | COMPRESSOR C-2101-A SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
171 | 3 | ESD 3-B-LAMP | COMPRESSOR C-2101-B SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
172 | 3 | ESD 3-C-LAMP | COMPRESSOR C-2101-C SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
173 | 0 | ESD0-PB | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
174 | 1A | ESD1A-PB | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
175 | 2A | ESD2A-A-PB | TRAIN A SHUT DOWN WITH DEPRESSURIZING (ESD2A-A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
176 | 2A | ESD2A-B-PB | TRAIN B SHUT DOWN WITH DEPRESSURIZING (ESD2A-B) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
177 | 2A | ESD2A-C-PB | TRAIN C SHUT DOWN WITH DEPRESSURIZING (ESD2A-C) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
178 | --- | ESD-INH | ESD INHIBIT SELECTOR SWITCH | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
179 | --- | ESD-RST | RESET P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
180 | 1 | ESD1-PB | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
181 | 2 | ESD2-A-PB | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
182 | 2 | ESD2-B-PB | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-B) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
183 | 2 | ESD2-C-PB | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-C) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
184 | 3 | ESD 3-A-PB | COMPRESSOR C-2101-A SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
185 | 3 | ESD 3-B-PB | COMPRESSOR C-2101-B SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
186 | 3 | ESD 3-C-PB | COMPRESSOR C-2101-C SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 DELETED
187 | 0 | ESDI 0-EX | EXISTING SYSTEM ESD 0 status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | IF REQUIRED | D03 DELETED
188 | 1 | ESDI 1-EX | EXISTING SYSTEM ESD 1 status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D03 MODIFIED
189 | 1A | ESDI 1A-EX | EXISTING SYSTEM ESD 1A status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | IF REQUIRED | D03 DELETED
190 | 0 | ESDI 0- NEW | NEW SYSTEM ESD 0 SATATUS TO EXISTING SYSTEM | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 MODIFIED
191 | 1 | ESDI 1- NEW | ESD 1 status | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 MODIFIED
192 | 1A | ESDI 1A- NEW | ESD 1A status | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 MODIFIED
193 | 0 | ESDI 0-DCS | ESD 0 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
194 | 1 | ESDI 1-DCS | ESD 1 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
195 | 1A | ESDI 1A-DCS | ESD 1A status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
196 | 2 | ESDI 2-A-DCS | ESD 2 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
197 | 2 | ESDI 2-B-DCS | ESD 2 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
198 | 2 | ESDI 2-C-DCS | ESD 2 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
199 | 2A | ESDI 2A-A-DCS | ESD 2A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
200 | 2A | ESDI 2A-B-DCS | ESD 2A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
201 | 2A | ESDI 2A-C-DCS | ESD 2A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
202 | 3 | ESDI 3-A-DCS | ESD 3 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
203 | 3 | ESDI 3-B-DCS | ESD 3 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
204 | 3 | ESDI 3-C-DCS | ESD 3 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
205 | - | ESDI 3A-A-DCS | ESD 3A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
206 | - | ESDI 3A-B-DCS | ESD 3A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
207 | - | ESDI 3A-C-DCS | ESD 3A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D03 DELETED
| 0 | ESD 0-EL3A | 24 V DC UPS-002-CH01 Isolation Command | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
| 0 | ESD 0-EL3B | 24 V DC UPS-002-CH02 Isolation Command | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
| 0 | ESD 0-EL4A | 110 V DC Charger-001-CH01 Isolation Command | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
| 0 | ESD 0-EL4B | 110 V DC Charger-001-CH02 Isolation Command | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | ELECTRICAL (CHARGER) |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D03 ADDED
;
D03