## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0011_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1098 |  |  | Transmital Date: 20-Jun-2022
Document Title: Wiring Diagram For Interposing Relay Panel (IRP) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1098 |  |  | Transmital Date: 20-Jun-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DG-0011_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مدرک Instrument/F&G Cable List به عنوان مدرک مرجع ذکر گردد. |  | 1401-2294-172868 | 1401-05-20 | اعمال گردید.
2 | جهت هر کابل ارتباطی DCS با IRP در قسمت رک و ترمینال در ابتدای ترمینال بلاک مربوطه، برچسب متناظر قرار گیرد. به عنوان نمونه جهت کابل IRP-DCS 2)40CORE) در ابتدای ترمینال بلاک های متناظر بر چسب های XDCS-02 وDI-02 قرار گیرد. |  | 1401-2294-172868 | 1401-05-20 | مطابق با نظر کارفرما برچسب ترمینالها اصلاح گردید. لازم به ذکر است این مدرک می بایست توسط سازنده به طور کامل و دقیق تولید و ساخته شود. لذا این موارد برطرف خواهد گردید.
3 | جهت سیگنال های ESD و DCS ظرفیت حداقل 20 درصد SPARE در نظر گرفته شود. |  | 1401-2294-172868 | 1401-05-20 | ظرفیت Spare به طور کامل در نظر گرفته شده است.
4 | جهت هر کابل ارتباطی ESD و IRP در قسمت رک و ترمینال در ابتدای ترمینال بلاک مربوطه،برچسب متناظر قرار گیرد. بعنوان نمونه جهت کابل IRP-ESD 2)40CORE) در ابتدای ترمینال بلاک های متناظر بر چسب های XESD-02 و DO-02 قرار گیرد. |  | 1401-2294-172868 | 1401-05-20 | مطابق با نظر کارفرما برچسب ترمینالها اصلاح گردید. لازم به ذکر است این مدرک می بایست توسط سازنده به طور کامل و دقیق تولید و ساخته شود. لذا این موارد برطرف خواهد گردید.
5 | در حد امکان فضای خالی،بین ترمینال بلاک های هر کابل با کابل مجاور در نظر گرفته شود. |  | 1401-2294-172868 | 1401-05-20 | این فضا می بایست در زمان ساخت به سازنده یادآوری شود که این امر اتفاق خواهد افتاد. همچنین با توجه به فضای Spare در نظر گرفته شده، فضای خالی تعبیه شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saaadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 05-Jul-22 |  |  |  |  | Date: