## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0011_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1098 |  |  | Transmital Date: 20-Jun-2022
Document Title: Wiring Diagram For Interposing Relay Panel (IRP) |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1098 |  |  | Transmital Date: 20-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0011_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFC after finalizing or minor comments on below prerequisite documents: -I/O List for control system -I/O List for ESD system -Electrical I/O Signal List |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد.
2 | Required connection between IRP and MV/LV switchgears incomings, Coupling and outgoing feeders, AC/DC UPS, Diesel generator Control panel, Transformers alarm window, packages control panel, etc. shall be added to this document. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد.
3 | Switchgear tag number of MV/LV switchgear and related terminal number shall be added to document. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد.
4 | the cables between IRP and DCS/EDS shall be multi pair type instead of multi core. (for example 40 Pair x 1.5) |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد.
5 | status signals will be considered Digital Input (DI) and command signals will be considered Digital Output (DO) from the DCS/ESD point of view. Therefor in order to facilitate in wiring to DI and DO cards, its proposed to considering separate multi pair cables for DI and DO signals between IRP and DCS/ESD marshaling panel. |  | BK-SUR-ENG-ELE-01-04986 | 2022-07-05 | تغییرات اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 05-Jul-22 |  |  |  |  | Date: