## Air
Instrument & Plant Air Consumption
Instrument & Plant Air Consumption | [5 empty] | Inlet Nozzle Sizing
Item | Qty. |  | Unit Cons. | Total Cons. | Unit |  | Variable |  | Unite
On/Off Valve | 32 | 100% | 0.64 | 20.48 | Nm3/hr | A constant used during inlet nozzle sizing | ɛ | 6000
Control Valve | 29 | 100% | 0.64 | 18.56 | Nm3/hr | A constant used during gas outlet nozzle sizing | X | 3750
Dehydration | 1 | 100% | 14 | 14 | Nm3/hr | Gas Density | ρv | 9.3 | Kg/m3
Variable Pitch air cooler | 6 | 100% | 1 | 21 | Nm3/hr | Gas Flowrate | Qv | 19.8649 | m3/hr
Gas Compressor Instrument Air | 3 | 100% | 6 | 18 | Nm3/hr | Liquid Density | ρL | 9.3 | Kg/m3
Total Instrument Air Consumption | - |  |  | 92.04 | Nm3/hr | Liquid Flowrate | QL | 0.01
30% Over Design |  |  |  | 119.652 | Nm3/hr | ( Inlet mixture density ) | ρin | 9.3 | Kg/m3
Total Instrument Air Consumption |  |  |  | 119.652 | Nm3/hr |  | Vin | 25.4 | m/s
Air Dryer Regenration |  |  | 20% | 23.9304 | Nm3/hr | The product (ρin*Vin^2 )shall not exceed ɛ | ρin Vin^2 | TRUE
Dryer Inlet |  |  |  | 143.5824 | Nm3/hr |  | Ain | 0.00021735 | m2
Plant Air |  |  |  | 30 | Nm3/hr | Calculated inlet nozzle diameter | Din | 0.65495 | in
Air Compressor Outlet |  |  |  | 173.5824 | Nm3/hr |  | Selected Nozzle | 2 | in
109.64 |  | 39.04 |  | 190.9406 |  | Note : ε should be 1000 when no inlet device is foreseen. ε should be 1500 when a half-open pipe is used. ε should be 6000 when a vane pack is used
Air Receiver Capacity
Item | Value | Unit
Barometric Pressure P0 | 1.03
Initial Air Receiver Pressure P1 | 9.03 | bara |  |  | 0.81673 | Gas Outlet Nozzle Sizing
Final Air Receiver Pressure P2 | 5.53 | bara |  |  | 0.68 |  | Variable |  | Unite
Air Receiver Retention time | 15 | min |  |  | 0.83258 | A constant used during inlet nozzle sizing | ɛ | 6000
Total Plant Air Consumption | 119.652 | Nm3/hr |  |  |  | A constant used during gas outlet nozzle sizing | X | 3750
Total Plant Air Consumption | 126.2227 | Sm3/hr |  |  |  | Gas Density | ρv | 9.3 | Kg/m3
Max. Air Receiver Required Vol. | 9.2864 | m3 |  |  |  | Gas Flowrate | Qv | 19.8649 | m3/hr
[6 empty] | Liquid Density | ρL | 9.3 | Kg/m3
Air Receiver Sizing (Vertical) | [5 empty] | Liquid Flowrate | QL | 0.01
Item | Value | Unit | Value | Unit |  | ( Inlet mixture density ) | ρin | 9.3 | Kg/m3
Height (H) | 5000 | mm | 5 | m |  |  | VgOut | 20.0805 | m/s
Diameter (ID) | 1500 | mm | 1.5 | m |  | The product (ρin Vin^2 )shall not exceed ɛ | ρin*Vin^2 | TRUE
Radius | 750 | mm | 0.75 | m |  |  | AgOut | 0.0002748 | m2
Type of Head | Elliptical |  |  |  |  | Calculated inlet nozzle diameter | DgOut | 0.73642 | in
Depth of Head | 375 | mm | 0.375 | m |  |  | Selected Nozzle | 2 | in
Liquid Level | 300 | mm | 0.3 | m | 8.8313
Nominal Capacity | 9.7193 |  | m3 | 9.2864
Note on D6: Roshanak Haditalab: Without BDV
Note on F6: Roshanak Haditalab: Based on IPS-E-PR-330.
Note on F7: Roshanak Haditalab: Based on IPS-E-PR-330.
Note on M17: Ghazale Ataie: Minimum nozzle size=2 in
Note on M35: Ghazale Ataie: Minimum nozzle size=2 in

## Nitrogen
Nitrogen Consumption
Item | Qty. | Unit Cons. | Total Cons. | Unit | Lean Glycol Storage Tank |  |  | Glycol Sump Drum
Gas Compressor | 3 | 6 | 18 | Nm3/hr | Height | 5 | m | Height | 1.1 | m
Methanol Injection Pack. | 0 | 1 | 0 | Nm3/hr | LL | 0.6 | m | LL | 0.15 | m
Lean Glycol Tank Blanketing | 1 | N.A. | 9.3444 | Nm3/hr | V | 55.292 | m3 | V | 3.4718 | m3
| 1 | N.A. | 9.34 x 30% | Nm3/hr | 0.169 Nm3 per Emoty Cubic | 9.3444 | Nm3/h | 0.169 Nm3 per Emoty Cubic | 0.58673 | Nm3/h
Glycol Sump Vessel | 1 | N.A. | 0.58673 | Nm3/hr
| 1 | N.A. | 0.59 x 30% | Nm3/hr
Total Nitrogen |  |  | 30.9104 | Nm3/hr | Calculated based on :
Total + 10% Over Design |  |  | 34.0015 | Nm3/hr | For tanks smaller than 3180 m3 (20000 bbl) the venting requirement due to thermal contraction is limited by the maximum temperature change of 56 K/h (100 °R/h) in the tank’s vapour space. Using an initial temperature of 48.9 °C (120 °F), venting requirement is approximately equal to 0.169 Nm3 of air per cubic meter.(1 SCFH of air per barrel) of empty tank volume.
Plant Air |  | 4 | 123.6416 | Nm3/hr
|  |  | 136.0058 | 149.6064
Nitrogen Receiver Vessel Sizing
Item | Value | Unit
Barometric Pressure P0 | 1.03
Initial Air Receiver Pressure P1 | 9.03 | bara
Final Air Receiver Pressure P2 | 5.03 | bara
Air Receiver Retention time | 15 | min |  |  | Lean Glycol Storage Tank |  |  | Glycol Sump Drum
Total Plant Nitrogen Consumption | 34.0015 | Nm3/hr |  |  | Diameter | 4 | m | TL-TL | 3.6 | m
Total Plant Nitrogen Consumption | 35.8686 | Sm3/hr |  |  | TL-TL | 5 | m | Diameter | 1.1 | m
Max. Nitrogen Receiver Required Vol. | 2.309 | m3 |  |  | LLL | 0.6 | m | Radius | 0.55 | m
[5 empty] | Nominal Capacity | 62.8 | m3 | Depth of Head | 0.275 | m
Nitrogen Receiver Sizing (Vertical) |  |  |  |  | Capacity from Bott to LLL | 7.536 | m3 | HLL | 0.8 | m
Item | Value | Unit | Value | Unit | Capacity from Bott to HLL | 56.52 | m3 | LLLL | 0.15 | m
Height (H) | 3150 | mm | 3.15 | m | Working Capacity | 55.264 | m3 | Nominal Capacity | 3.7696 | m3
Diameter (ID) | 1050 | mm | 1.05 | m |  |  |  | Vol. from Bottom to HLL | 2.9502 | m3
Radius | 525 | mm | 0.525 | m |  |  |  | Vol. from Bottom to LLL | 0.29786 | m3
Type of Head | Elliptical | [6 empty] | Working Capacity | 2.6523 | m3
Depth of Head | 262.5 | mm | 0.2625 | m
Liquid Level | 300 | mm | 0.3 | m
Nominal Capacity | 3.0307 |  | m3 | 2.309
Note on F13: Roshanak Haditalab: 3 ~ 4

## Potable Water
Tank Sizing (Vertical)
Item | Value | Unit
Height (H) | 2.6 | m
Diameter (ID) | 3.5 | m
HLL | 2.25 | m
LLL | 0.15 | m
Nominal Capacity | 25.0023 | m3
Working Capacity | 20.1941 | m3 | 20
Elevation | 6 | m
Water Consumption
Person | 10
Usage | 100 | lit/day.person
Usage | 0.1 | m3/day.person
Total Consumption | 1 | m3/day
Hold-Up | 20 | day
Total Vol. | 20 | m3
Usage | 0.041667 | m3/hr

## Closed Drain drum
Vessel Sizing (Horizontal) |  |  |  |  | Vessel Sizing (Horizontal) Slug Catcher |  |  |  |  | Vessel Sizing (Horizontal) Slug Catcher
Item | Value | Unit | Value | Unit | Item | Value | Unit | Value | Unit | Item | Value | Unit | Value | Unit
Length (L) | 7800 | mm | 7.8 | m | Length (L) | 12600 | mm | 12.6 | m | Length (L) | 12600 | mm | 12.6 | m
Diameter (ID) | 2600 | mm | 2.6 | m | Diameter (ID) | 4200 | mm | 4.2 | m | Diameter (ID) | 4500 | mm | 4.5 | m
Radius | 1300 | mm | 1.3 | m | Radius | 2100 | mm | 2.1 | m | Radius | 2250 | mm | 2.25 | m
Type of Head | Elliptical |  |  |  | Type of Head | Elliptical |  |  |  | Type of Head | Elliptical
Depth of Head | 650 | mm | 0.65 | m | Depth of Head | 1050 | mm | 1.05 | m | Depth of Head | 1125 | mm | 1.125 | m
HHLL | 2300 | mm | 2.3 | m | HHLL | 3900 | mm | 3.9 | m | HHLL | 3600 | mm | 3.6 | m
HLL | 2150 | mm | 2.15 | m | HLL | 3800 | mm | 3.8 | m | HLL | 3500 | mm | 3.5 | m
LLL | 300 | mm | 0.3 | m | LLL | 250 | mm | 0.25 | m | LLL | 250 | mm | 0.25 | m
LLLL | 150 | mm | 0.15 | m | LLLL | 150 | mm | 0.15 | m | LLLL | 150 | mm | 0.15 | m
Nominal Capacity | 46.0139 |  | m3 |  | Nominal Capacity | 193.9619 |  | m3 |  | Nominal Capacity | 224.2508 |  | m3
Vol. from Bottom to HLL | 40.8574 |  | m3 |  | Vol. from Bottom to HLL | 185.0108 |  | m3 |  | Vol. from Bottom to HLL | 188.0813 |  | m3
Vol. from Bottom to LLL | 2.8277 |  | m3 |  | Vol. from Bottom to LLL | 4.424 |  | m3 |  | Vol. from Bottom to LLL | 4.5925 |  | m3
Working Capacity | 38.0297 |  | m3 |  | Working Capacity | 180.5868 |  | m3 | 37.3 | Working Capacity | 183.4888 |  | m3 | 37.3
Elevation | - |  | m |  | Elevation | - |  | m |  | Elevation | - |  | m
Based on Slug Catcher drum bottom to LLL . & Inlet K.O. Drum bottom to HLL.
Vessel Sizing (Horizontal) Inlet K.O. drum
[5 empty] | Item | Value | Unit | Value | Unit
[5 empty] | Length (L) | 4500 | mm | 4.5 | m
[5 empty] | Diameter (ID) | 1500 | mm | 1.5 | m
[5 empty] | Radius | 750 | mm | 0.75 | m
[5 empty] | Type of Head | Elliptical
[5 empty] | Depth of Head | 375 | mm | 0.375 | m
[5 empty] | HHLL | 1200 | mm | 1.2 | m
[5 empty] | HLL | 1050 | mm | 1.05 | m
[5 empty] | LLL | 800 | mm | 0.8 | m
[5 empty] | LLLL | 150 | mm | 0.15 | m
[5 empty] | Nominal Capacity | 8.8357 |  | m3
[5 empty] | Vol. from Bottom to HLL | 6.6384 |  | m3
[5 empty] | Vol. from Bottom to LLL | 4.7992 |  | m3
[5 empty] | Working Capacity | 1.8392 |  | m3 | 37.3
[5 empty] | Elevation | - |  | m
Note on O17: Roshanak Haditalab: Based on slug catcher drum capacity from bottom to NLL. ID: 3600 mm, L:10800 mm, NLL: 1500 mm
Note on U17: Roshanak Haditalab: Based on slug catcher drum capacity from bottom to NLL. ID: 3600 mm, L:10800 mm, NLL: 1500 mm
Note on O36: Roshanak Haditalab: Based on slug catcher drum capacity from bottom to NLL. ID: 3600 mm, L:10800 mm, NLL: 1500 mm

## Glycol Sump Drum
Vessel Sizing (Horizontal)
Item | Value | Unit | Value | Unit
Length (L) | 3600 | mm | 3.6 | m
Diameter (ID) | 1100 | mm | 1.1 | m
Radius | 550 | mm | 0.55 | m
Type of Head | Elliptical
Depth of Head | 275 | mm | 0.275 | m
HHLL | 800 | mm | 0.8 | m
HLL | 650 | mm | 0.65 | m
LLL | 300 | mm | 0.3 | m
LLLL | 150 | mm | 0.15 | m
Nominal Capacity | 3.7696 |  | m3
Vol. from Bottom to HLL | 2.3256 |  | m3
Vol. from Bottom to LLL | 0.81945 |  | m3
Working Capacity | 1.5062 |  | m3 | 1.5
Elevation | - |  | m
Note on G17: Roshanak Haditalab: Besed on vendor data.

## Oily Sump
Rain Rate
Item | Value | Unit
Length 1 | 170 | m
Width 1 | 27 | m
Length 2 | 18 | m
Width 2 | 10.5 | m
Length 3 | 8 | m
Width 3 | 6 | m
Length 4 |  | m
Width 4 |  | m
Area | 4827 | m2
Max. Rainfall | 101.51 | mm/hr
Max. Rainfall | 0.10151 | m/hr
Max. Rainfall | 0.0016918 | m/min
Max. Rainfall | 0.00084592 | m/min
Sump Sizing
Item | Value | Unit
Hold-Up time | 15 | min
Rainfall | 0.012689 | m
Rain Volume | 61.2486 | m3
Length (L) | 3 | m
Hight (H) | 3 | m
Width (W) | 4 | m
HLL | 2.7 | m
Full Volume | 36 | m3
Usable Volume | 32.4 | m3 | 61.2486
Note on D5: Roshanak Haditalab: Based on piping plot plan.
Note on D6: Roshanak Haditalab: Based on piping plot plan.
Note on D7: Roshanak Haditalab: Based on piping plot plan.
Note on D8: Roshanak Haditalab: Based on piping plot plan.
Note on D14: Roshanak Haditalab: Based on client's data.

## fuel gas
purge gas pressure
| barg | ft/s | m/s | in | m | A(m2) | Am3/s | Am3/hr | kg/hr
Flare header size | 0.5 | 0.1 | 0.03048 | 10 | 0.254 | 0.050671 | 0.0015444 | 5.56 | 21
ignition panel cosumption | [8 empty] | 5
Dehydration | [8 empty] | 30
Blanketing | [7 empty] | 10 | 14

## Slug Catcher
FIRE WATER |  |  | DISEIL GENERATOR
Fuel Oil Storage Drum Calculation |  |  | Fuel Oil Storage Drum Calculation
Drum Diameter | 1.2 | m | Drum Diameter | 1.5 | m
Drum Length | 3 | m | Drum Length | 3 | m
Drum Total Volume | 3.6644 | m3 | Drum Total Volume | 5.9641 | m3
Maximum Fuel Oil Consumption | 2.7 | m3/hr | Maximum Fuel Oil Consumption | 5 | m3/hr
HLL | 0.95 | m | HLL | 1.25 | m
LLL | 0.15 | m | LLL | 0.15 | m
Liquid Volume HLL | 3.1218 | m3 | Liquid Volume HLL | 5.3343 | m3
Liquid Volume LLL | 0.25645 | m3 | Liquid Volume LLL | 0.29446 | m3
Storage Volume (between HLL & LLL) | 2.8654 | m3 | Storage Volume (between HLL & LLL) | 5.0398 | m3
Slug Catcher, Working Capacity
|  |  | Drum Diameter | 4.2 | m
|  |  | Drum Length | 12.6 | m
|  |  | Drum Total Volume | 215.2977 | m3
|  |  | HLL | 3.8 | m
|  |  | LLL | 0.25 | m
|  |  | Liquid Volume HLL | 205.8029 | m3
|  |  | Liquid Volume LLL | 4.6418 | m3
|  |  | Storage Volume (between HLL & LLL) | 201.1611 | m3

## Diesel Oil
Corrosion Consumption
Injec. Point | Qty. | Q max. | Q max. total | Q min. | Unit | Corr. max. | Corr. min. | Diesel max. | Diesel min. | Rated | Q total max. | Q total min. | Unit
Gas From Binak (PR-1002) | 1 | 4.921 | 4.921 | 4.921 | (MMSCFD) | 0.09637 | 0.09637 | 0.22486 | 0.22486 | 0.11564 | 0.32123 | 0.32123 | lit/hr | 4.921
Gas From Golkhari (PR-2002) | 1 | 9.5285 | 9.5285 | 9.5285 | (MMSCFD) | 0.1866 | 0.1866 | 0.4354 | 0.4354 | 0.22392 | 0.622 | 0.622 | lit/hr | 9.5285
V-2105 Outlet | 1 | 14.6001 | 14.6001 | 14.6001 | (MMSCFD) | 0.28592 | 0.28592 | 0.66714 | 0.66714 | 0.3431 | 0.95306 | 0.95306 | lit/hr | 14.6001
V-2103 Outlet | 1 | 14.1028 | 14.1028 | 14.1028 | (MMSCFD) | 0.27618 | 0.27618 | 0.64442 | 0.64442 | 0.33142 | 0.9206 | 0.9206 | lit/hr | 14.1028
V-2205 Outlet | 1 | 0.41408 | 0.41408 | 0.41408 | (MMSCFD) | 0.008109 | 0.008109 | 0.018921 | 0.018921 | 0.0097308 | 0.02703 | 0.02703 | lit/hr | 0.41408
Pipeline (PL-3201) | 1 | 14.0275 | 14.0275 | 14.0275 | (MMSCFD) | 0.2747 | 0.2747 | 0.64098 | 0.64098 | 0.32965 | 0.91568 | 0.91568 | lit/hr | 14.0275
V-2104 Outlet | 1 | 9.5998 | 9.5998 | 9.5998 | (MMSCFD) | 0.188 | 0.188 | 0.43866 | 0.43866 | 0.2256 | 0.62666 | 0.62666 | lit/hr | 9.5998
Total |  |  | 57.5939 | 67.1937 | (MMSCFD) | 1.1279 | 1.1279 | 2.6317 | 2.6317 | 1.3535 | 4.3863 | 4.3863 | lit/hr
Total | [6 empty] | 0.56889 |  |  |  | 0.0043863 | 0.0043863 | m3/hr | 0.10527
[7 empty] | 0.577 |  |  |  | 0.10527 |  | m3/day | 1.5791 | 14 DAY | 60 BAR PUMP
Diesel Generator Consumption
Generato Size | 500 | kW
Diesel Consumption | 35.7 | gal/hr
Diesel Consumption | 0.13495 | m3/hr
Diesel Consumption | 3.2387 | m3/day
0.26515
Fire Diesel Pump Consumption
Qty. | 1
Rated Capacity | 454 | m3/hr
Diff. Pressure | 10.3 | bar
Density | 850 | kg/m3
Hydraulic Power | 129.8944 | kW
Total Hydraulic Pow. | 129.8944 | kW
Efficiency | 72%
BHP | 180.409
Diesel Consumption | 114.3793 | lit/hr
Diesel Consumption | 11.4379 | lit/hr
Diesel Consumption | 0.12582 | m3/hr |  | 4.5294
Diesel Consumption | 3.0196 | m3/day
Total Diesel Consumption
Total Diesel Cons. | 0.26515 | m3/hr
Total Diesel Cons. | 6.3636 | m3/day
Hold-Up Time | 4 | day
Working Capacity | 25.4543 | m3
Vessel Sizing (Horizontal)
Item | Value | Unit | Value | Unit
Length (L) | 6000 | mm | 6 | m
Diameter (ID) | 2300 | mm | 2.3 | m
Radius | 1150 | mm | 1.15 | m
Type of Head | Elliptical
Depth of Head | 575 | mm | 0.575 | m
HLL | 2050 | mm | 2.05 | m
LLL | 150 | mm | 0.15 | m
Nominal Capacity | 28.1139 |  | m3
Vol. from Bottom to HLL | 26.543 |  | m3
Vol. from Bottom to LLL | 0.72976 |  | m3
Working Capacity | 25.8132 |  | m3 | 25.4543
Elevation | - |  | m
Note on K5: Roshanak Haditalab: Based on 70/30 in yellow row.
Note on D17: Roshanak Haditalab: Based on vendor data.
Note on D30: Roshanak Haditalab: 0.634 lit/ per kW per hour
Note on D31: Roshanak Haditalab: plus 5 percent volume for expansion and 5 percent volume for sump
Note on G32: Mohsen Ariafar: AS PER STANDARD 36 HOURS STORAGE