## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-CN-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1530 |  |  | Transmital Date: 10/23/2022
Document Title: CALCULATION NOTE FOR DRUM SIZING |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1530 |  |  | Transmital Date: 10/23/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-CN-0002_D05 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | محاسبات انجام شده در بند 7 مدرک ارسالی می بایست مورد بررسی مجدد و اصلاح قرار گیرد.به عنوان مثال می توان به طول و قطر مخزن اشراره نمود. |  | 1401-2294-380515 | 1401/10/09 | اصلاح گردید.
2 | در خصوص پاسخ آن پیمانکار به کامنت شماره 1، ابعاد مخزن در مطالعات مقدماتی 2300*6000 می باش. در ویرایش پیشین بیشینه مصرف (supply fuel oil to all the users for a minimum of 5 days of continuous operation.) لحاظ گردیده است،در صورتی که در مدرک ارسالی کاهش پیدا کرده است.لذا ضروری است اسناد پیمان مورد مطالعه مجدد و بررسی و محاسبات لازم از جانب آن پیمانکار انجام پذیرد. |  | 1401-2294-380515 | 1401/10/09 | مورد بررسی و اصلاح قرار گرفت.
3 | ضروریست مدرک مذکور با آخرین ویرایش مدارک از جمله P&ID یکسان سازی به عمل آید. |  | 1401-2294-380515 | 1401/10/09 | بروز رسانی مطابق با سایر مدارک صورت گرفته است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: