## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 11
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | LI | 0009 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | JAN.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | AUG.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708010
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 11
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0009 |  | D01
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 |  | X | [6 empty] | 74
11 |  | X | [6 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes & References
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 11
9184 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO | 110 | IN | LI |  | 0009 | D01
GENERAL NOTES:
1- Cable length will be finalized after approval of Instrument location.
2- Gland Size will be finalized after Instrument Cable/Cable Gland P.O
3- Cutting column/Drum no. will be finalized after cable P.O.
4- All cables shall be accordance with Flame retardant standard IEC 60332
5- Fire Resistant cables shall be accordance with standard IEC 60331.
6- All conductors shall be accordance with standard IEC 60228 and the material shall be Tinned cupper.
7- Outer sheath Material :
Flame Retardant : PVC , Color : Light Blue for I.S. & Gray for N.I.S
Fire Resistant : PVC , Color : Light Blue with Red Strip for I.S. & Gray with Red Strip for N.I.S & Red for F&G
[6 empty] | 8- Cable type legend : | [9 empty] | 9- Junction Box Numbering : :
[5 empty] | X - X X - X - X | [9 empty] | JBX - X - XXXX
| BL: Light Blue | [8 empty] | F: Fire resistance | [6 empty] | Sequence No.
| BR: Light Blue/Red Strip | [8 empty] | FA: Fire resistance, Armoured
| GY: Gray | [8 empty] | A: Armoured | [6 empty] | A : Analoge
| GR: Gray /Red Strip | [8 empty] | N: None | [6 empty] | D : Digital
| RD: Red | [15 empty] | S : Solenoid
D : DCS
| Number of core | [15 empty] | E : ESD
| or pair or triad | [10 empty] | 1: 1 mm² |  |  |  |  | F : F&G
2: 1.5 mm²
3: 2.5 mm²
[7 empty] | P: Pair |  |  |  |  | 4: 6 mm²
[7 empty] | C: Core |  |  |  |  | 5: 16 mm²
[7 empty] | T: Triad |  |  |  |  | 6: 35 mm²
REFERENCES:
| 1 | BK-W007S-PEDCO-110-IN-LI-0002_D02 IO LIST FOR CONTROL SYSTEM
| 2 | BK-W007S-PEDCO-110-IN-LI-0003_D02 IO LIST FOR ESD SYSTEM
| 3 | BK-W007S-PEDCO-110-IN-LI-0004_D00 IO LIST FOR F&G SYSTEM
| 4 | BK-GNRAL-PEDCO-000-IN-SP-0010-D02 SPECIFICATION FOR INSTRUMENT & F&G CABLES
| 5 | BK-W007S-PEDCO-110-IN-DG-0009_D01-INSTRUMENT & F&G JUNCTION BOX TERMINATION DIAGRAM - EXTENSION OF BINAK BC MANI
ABBREVIATION :
| 1- CU |  | : Conductor (Standard tinned copper)
| 2- XLPE |  | : Insulation (Cross-linked polyethylene, low smoke, zero halogen)
| 3- DW |  | : Drain Wire
| 4- ISC |  | : Individual Screen
| 5- DW |  | : Drain Wire
| 6- OSC |  | : Overall Screen
| 7- PVC |  | : Inner sheath (polyvinyl chloride insulation )
| 8- SWB |  | : Armoure (Steel wire Braided )
| 9- PVC |  | : Outer sheath (polyvinyl chloride insulation)
| 10- FRT |  | : Flame Retardant
| 11- FRS |  | : Fire Resistant
D01

## SUMMARY
| NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 11
| 9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | LI | 0009 | D01
SUMMARY
| ITEM | TYPE | DESCRIPTION | [6 empty] | QUANTITY (m)(NOTE1)
[10 empty] | ACTUAL (m) |  | (PLUS 20%) (m)
| 1 | BL-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 285 |  | 342
| 2 | BL-12P-1-A | 12 PAIR * 1 mm² , CU/XLPE/DW/ISC/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 300 |  | 360
| 3 | GY-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 180 |  | 216
| 4 | GY-20P-1-A | 20 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/SWA/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 130 |  | 156
| 5 | BR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/ISC/PVC/SWA/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 90 |  | 108
| 6 | BR-12P-1-FA | 12 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 100 |  | 120
| 7 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 90 |  | 108
| 8 | GR-12P-3-FA | 12 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 70 |  | 84
| 9 | GR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWA/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 90 |  | 108
| 10 | RD-1P-2-F | 1 PAIR * 1.5 mm² (SERIAL CABLE), CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED ( BY VENDOR FACP) | [6 empty] | 199 |  | 238.8
| 11 | RD-1P-2-FA | 1 PAIR * 1.5 mm² (SERIAL CABLE), CU/Mica-tape/XLPE/DW/OSC/PVC, SWA/PVC Fire resistant (IEC-60331)-RED ( BY VENDOR FACP) | [6 empty] | 686 |  | 823.2
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
D01

## Cable list
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | W007S | PEDCO | 110 |  | IN |  | LI | 0009 | D01
ITEM | Cable Code | Tag No. | Description | Cable No. |  | From | To. | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BL-1P-2-A | PT-1702A | Pressure Transmitter | IC- | PT-1702A | PT-1702A | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
2 | BL-1P-2-A | PT-1702B | Pressure Transmitter | IC- | PT-1702B | PT-1702B | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
3 | BL-1P-2-A | PT-1702C | Pressure Transmitter | IC- | PT-1702C | PT-1702C | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
4 | BL-1P-2-A | PT-1702D | Pressure Transmitter | IC- | PT-1702D | PT-1702D | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
5 | BL-1P-2-A | PT-1702E | Pressure Transmitter | IC- | PT-1702E | PT-1702E | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
6 | BL-1P-2-A | PT-1702F | Pressure Transmitter | IC- | PT-1702F | PT-1702F | JBD-A-17001 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
7 | BL-12P-1-A | JBD-A-17001 | Junction Box | MC- | JBD-A-17001 | JBD-A-17001 | DCS | FRT | SWA | IS | 12 | Pair | 1 | Individual & Overal Screen | Light Blue | Note 1 | 300/500 V | 100 | M40
8 | BL-1P-2-A | FT-1701A | Flow Transmitter | IC- | FT-1701A | FT-1701A | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
9 | BL-1P-2-A | FT-1701B | Flow Transmitter | IC- | FT-1701B | FT-1701B | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
10 | BL-1P-2-A | FT-1701C | Flow Transmitter | IC- | FT-1701C | FT-1701C | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
11 | BL-1P-2-A | FT-1701D | Flow Transmitter | IC- | FT-1701D | FT-1701D | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
12 | BL-1P-2-A | FT-1701E | Flow Transmitter | IC- | FT-1701E | FT-1701E | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
13 | BL-1P-2-A | FT-1701F | Flow Transmitter | IC- | FT-1701F | FT-1701F | JBD-A-17002 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
14 | BL-12P-1-A | JBD-A-17002 | Junction Box | MC- | JBD-A-17002 | JBD-A-17002 | DCS | FRT | SWA | IS | 12 | Pair | 1 | Individual & Overal Screen | Light Blue | Note 1 | 300/500 V | 100 | M40
15 | BL-1P-2-A | FCV-1701A | Flow Control Valve | IC- | FCV-1701A | FCV-1701A | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
16 | BL-1P-2-A | FCV-1701B | Flow Control Valve | IC- | FCV-1701B | FCV-1701B | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
17 | BL-1P-2-A | FCV-1701C | Flow Control Valve | IC- | FCV-1701C | FCV-1701C | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
18 | BL-1P-2-A | FCV-1701D | Flow Control Valve | IC- | FCV-1701D | FCV-1701D | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
19 | BL-1P-2-A | FCV-1701E | Flow Control Valve | IC- | FCV-1701E | FCV-1701E | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
20 | BL-1P-2-A | FCV-1701F | Flow Control Valve | IC- | FCV-1701F | FCV-1701F | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
21 | BL-1P-2-A | LT-1701 | Level Transmitter | IC- | LT-1701 | LT-1701 | JBD-A-17003 | FRT | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue | Note 1 | 300/500 V | 15 | M20
22 | BL-12P-1-A | JBD-A-17003 | Junction Box | MC- | JBD-A-17003 | JBD-A-17003 | DCS | FRT | SWA | IS | 12 | Pair | 1 | Individual & Overal Screen | Light Blue | Note 1 | 300/500 V | 100 | M40
23 | GY-1P-2-A | EZSO-1701A | limit Switch Open | IC- | EZSO-1701A | EZSO-1701A | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
24 | GY-1P-2-A | EZSC-1701A | limit Switch Close | IC- | EZSC-1701A | EZSC-1701A | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
25 | GY-1P-2-A | EZSO-1701B | limit Switch Open | IC- | EZSO-1701B | EZSO-1701B | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
26 | GY-1P-2-A | EZSC-1701B | limit Switch Close | IC- | EZSC-1701B | EZSC-1701B | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
27 | GY-1P-2-A | EZSO-1701C | limit Switch Open | IC- | EZSO-1701C | EZSO-1701C | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
28 | GY-1P-2-A | EZSC-1701C | limit Switch Close | IC- | EZSC-1701C | EZSC-1701C | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
29 | GY-1P-2-A | EZSO-1701D | limit Switch Open | IC- | EZSO-1701D | EZSO-1701D | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
30 | GY-1P-2-A | EZSC-1701D | limit Switch Close | IC- | EZSC-1701D | EZSC-1701D | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
31 | GY-1P-2-A | EZSO-1701E | limit Switch Open | IC- | EZSO-1701E | EZSO-1701E | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
32 | GY-1P-2-A | EZSC-1701E | limit Switch Close | IC- | EZSC-1701E | EZSC-1701E | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
33 | GY-1P-2-A | EZSO-1701F | limit Switch Open | IC- | EZSO-1701F | EZSO-1701F | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
34 | GY-1P-2-A | EZSC-1701F | limit Switch Close | IC- | EZSC-1701F | EZSC-1701F | JBD-D-17001 | FRT | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray | Note 1 | 300/500 V | 15 | M20
35 | GY-20P-1-A | JBD-D-17001 | Junction Box | IC- | JBD-D-17001 | JBD-D-17001 | DCS | FRT | SWA | NIS | 20 | Pair | 1 | Overal Screen | Gray | Note 1 | 300/500 V | 70 | M50
36 | GY-20P-1-A | XR-1702 | Running | MC- | DMCC | MCC (IRP) | DCS | FRT | SWA | NIS | 12 | Pair | 1 | Overal Screen | Gray | Note 1 | 300/500 V | 50 | M40
|  | XF-1702 | Fault
|  | XL-1702 | Local / Remote
|  | XM-1702 | AUTO / MANUAL
|  | XST-1702 | Start Command | [16 empty] | Deleted
|  | XSP-1702 | Stop Command
37 | BR-1P-2-FA | PT-1701A | Pressure Transmitter | IC- | PT-1701A | PT-1701A | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
38 | BR-1P-2-FA | PT-1701B | Pressure Transmitter | IC- | PT-1701B | PT-1701B | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
39 | BR-1P-2-FA | PT-1701C | Pressure Transmitter | IC- | PT-1701C | PT-1701C | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
40 | BR-1P-2-FA | PT-1701D | Pressure Transmitter | IC- | PT-1701D | PT-1701D | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
41 | BR-1P-2-FA | PT-1701E | Pressure Transmitter | IC- | PT-1701E | PT-1701E | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
42 | BR-1P-2-FA | PT-1701F | Pressure Transmitter | IC- | PT-1701F | PT-1701F | JBE-A-17001 | FRS | SWA | IS | 1 | Pair | 1.5 | Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 15 | M20
43 | BR-12P-1-A | JBE-A-17001 | Junction Box | IC- | JBE-A-17001 | JBE-A-17001 | ESD | FRS | SWA | IS | 12 | Pair | 1 | Individual & Overal Screen | Light Blue/Red Strip | Note 1 | 300/500 V | 100 | M20
44 | GR-1P-3-FA | ESOV-1701A | Emergency Solenoid Valve | IC- | ESOV-1701A | ESOV-1701A | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
45 | GR-1P-3-FA | ESOV-1701B | Emergency Solenoid Valve | IC- | ESOV-1701B | ESOV-1701B | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
46 | GR-1P-3-FA | ESOV-1701C | Emergency Solenoid Valve | IC- | ESOV-1701C | ESOV-1701C | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
47 | GR-1P-3-FA | ESOV-1701D | Emergency Solenoid Valve | IC- | ESOV-1701D | ESOV-1701D | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
48 | GR-1P-3-FA | ESOV-1701E | Emergency Solenoid Valve | IC- | ESOV-1701E | ESOV-1701E | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
49 | GR-1P-3-FA | ESOV-1701F | Emergency Solenoid Valve | IC- | ESOV-1701F | ESOV-1701F | JBE-S-17001 | FRS | SWA | NIS | 1 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 15 | M20
50 | GR-12P-3-FA | JBE-S-17001 | Junction Box | IC- | JBE-S-17001 | JBE-S-17001 | ESD | FRS | SWA | NIS | 12 | Pair | 2.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 70 | M20
51 | GR-1P-2-FA | ESD-P-1701 | Emergency Trip Command | IC- | EMCC | ESD | MCC(IRP) | FRS | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 V | 50 | M20
52 | GR-1P-2-FA | ESDR 0-UPS | Emergency Shoutdown | IC- | UESD | UPS | ESD | FRS | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 20 | M20
53 | GR-1P-2-FA | ESDR -EXIST | Emergency Shoutdown | IC- | EESD | Existing ESD | ESD | FRS | SWA | NIS | 1 | Pair | 1.5 | Overal Screen | Gray /Red Strip | Note 1 | 300/500 vac | 20 | M20
54 | RD-1P-2-F | FACP | Fire Alaram Control Panel | IC- | FACP | FACP | HN-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 20 | M20
55 | RD-1P-2-F | HN-2101 | Horn | IC- | HN-2101 | HN-2101 | BR-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
56 | RD-1P-2-F | BR-2101 | Beacon | IC- | BR-2101 | BR-2101 | MAC-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
57 | RD-1P-2-F | MAC-2101 | Manual Call Point | IC- | MAC-2101 | MAC-2101 | BR-2102 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
58 | RD-1P-2-F | BR-2102 | Beacon | IC- | BR-2102 | BR-2102 | BL-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
59 | RD-1P-2-F | BL-2101 | Bell | IC- | BL-2101 | BL-2101 | SD-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
60 | RD-1P-2-F | SD-2101 | Smoke Detector | IC- | SD-2101 | SD-2101 | SD-2122 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
61 | RD-1P-2-F | SD-2122 | Smoke Detector | IC- | SD-2122 | SD-2122 | SD-2114 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
62 | RD-1P-2-F | SD-2114 | Smoke Detector | IC- | SD-2114 | SD-2114 | SD-2113 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
63 | RD-1P-2-F | SD-2113 | Smoke Detector | IC- | SD-2113 | SD-2113 | SD-2102 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
64 | RD-1P-2-F | SD-2102 | Smoke Detector | IC- | SD-2102 | SD-2102 | SD-2121 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
65 | RD-1P-2-F | SD-2121 | Smoke Detector | IC- | SD-2121 | SD-2121 | MAC-2104 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
66 | RD-1P-2-F | MAC-2104 | Manual Call Point | IC- | MAC-2104 | MAC-2104 | SD-2111 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
67 | RD-1P-2-F | SD-2111 | Smoke Detector | IC- | SD-2111 | SD-2111 | MAC-2103 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
68 | RD-1P-2-F | MAC-2103 | Manual Call Point | IC- | MAC-2103 | MAC-2103 | SD-2103 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
69 | RD-1P-2-F | SD-2103 | Smoke Detector | IC- | SD-2103 | SD-2103 | HD-2101 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
70 | RD-1P-2-F | HD-2101 | Heat Detector | IC- | HD-2101 | HD-2101 | SD-2105 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
71 | RD-1P-2-F | SD-2105 | Smoke Detector | IC- | SD-2105 | SD-2105 | SD-2112 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
72 | RD-1P-2-F | SD-2112 | Smoke Detector | IC- | SD-2112 | SD-2112 | SD-2106 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
73 | RD-1P-2-F | SD-2106 | Smoke Detector | IC- | SD-2106 | SD-2106 | SD-2104 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
74 | RD-1P-2-F | SD-2104 | Smoke Detector | IC- | SD-2104 | SD-2104 | MAC-2102 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 8 | M20
75 | RD-1P-2-F | MAC-2102 | Manual Call Point | IC- | MAC-2102 | MAC-2102 | FACP | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 20 | M20
76 | RD-1P-2-FA | FACP | Fire Alaram Control Panel | IC- | FACP | FACP | MAC-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 70 | M20
77 | RD-1P-2-FA | MAC-2201 | Manual Call Point | IC- | MAC-2201 | MAC-2201 | HD-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
78 | RD-1P-2-FA | HD-2201 | Heat Detector | IC- | HD-2201 | HD-2201 | HN-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
79 | RD-1P-2-FA | HN-2201 | Horn | IC- | HN-2201 | HN-2201 | BY-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
80 | RD-1P-2-FA | BY-2201 | Beacon | IC- | BY-2201 | BY-2201 | BR-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
81 | RD-1P-2-FA | BR-2201 | Beacon | IC- | BR-2201 | BR-2201 | SD-2201 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
82 | RD-1P-2-FA | SD-2201 | Smoke Detector | IC- | SD-2201 | SD-2201 | MAC-2202 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 3 | M20
83 | RD-1P-2-FA | MAC-2202 | Manual Call Point | IC- | MAC-2202 | MAC-2202 | FACP | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 70 | M20
84 | RD-1P-2-FA | HGD-2201 | Hydrogen Gas Detector | IC- | HGD-2201 | HGD-2201 | FACP | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 70 | M20
85 | RD-1P-2-FA | FACP | Fire Alaram Control Panel | IC- | FACP | FACP | MAC-2302 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 100 | M20
86 | RD-1P-2-FA | MAC-2302 | Manual Call Point | IC- | MAC-2302 | MAC-2302 | HN-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
87 | RD-1P-2-FA | HN-2301 | Horn | IC- | HN-2301 | HN-2301 | BR-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
88 | RD-1P-2-FA | BR-2301 | Beacon | IC- | BR-2301 | BR-2301 | BY-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
89 | RD-1P-2-FA | BY-2301 | Beacon | IC- | BY-2301 | BY-2301 | SD-2303 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
90 | RD-1P-2-FA | SD-2303 | Smoke Detector | IC- | SD-2303 | SD-2303 | SD-2316 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
91 | RD-1P-2-FA | SD-2316 | Smoke Detector | IC- | SD-2316 | SD-2316 | SD-2315 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
92 | RD-1P-2-FA | SD-2315 | Smoke Detector | IC- | SD-2315 | SD-2315 | HD-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
93 | RD-1P-2-FA | HD-2301 | Heat Detector | IC- | HD-2301 | HD-2301 | MAC-2303 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
94 | RD-1P-2-FA | MAC-2303 | Manual Call Point | IC- | MAC-2303 | MAC-2303 | LHD-2305 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
95 | RD-1P-2-FA | LHD-2305 | Linear Heat Detector | IC- | LHD-2305 | LHD-2305 | LHD-2304 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
96 | RD-1P-2-FA | LHD-2304 | Linear Heat Detector | IC- | LHD-2304 | LHD-2304 | SD-2313 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
97 | RD-1P-2-FA | SD-2313 | Smoke Detector | IC- | SD-2313 | SD-2313 | MAC-2304 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
98 | RD-1P-2-FA | MAC-2304 | Manual Call Point | IC- | MAC-2304 | MAC-2304 | LHD-2303 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
99 | RD-1P-2-FA | LHD-2303 | Linear Heat Detector | IC- | LHD-2303 | LHD-2303 | LHD-2302 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
100 | RD-1P-2-FA | LHD-2302 | Linear Heat Detector | IC- | LHD-2302 | LHD-2302 | SD-2312 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
101 | RD-1P-2-FA | SD-2312 | Smoke Detector | IC- | SD-2312 | SD-2312 | SD-2311 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
102 | RD-1P-2-FA | SD-2311 | Smoke Detector | IC- | SD-2311 | SD-2311 | SD-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
103 | RD-1P-2-FA | SD-2301 | Smoke Detector | IC- | SD-2301 | SD-2301 | LHD-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
104 | RD-1P-2-FA | LHD-2301 | Linear Heat Detector | IC- | LHD-2301 | LHD-2301 | SD-2314 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
105 | RD-1P-2-FA | SD-2314 | Smoke Detector | IC- | SD-2314 | SD-2314 | SD-2302 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 10 | M20
106 | RD-1P-2-FA | SD-2302 | Smoke Detector | IC- | SD-2302 | SD-2302 | BL-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
107 | RD-1P-2-FA | BL-2301 | Bell | IC- | BL-2301 | BL-2301 | BR-2302 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 1 | M20
108 | RD-1P-2-FA | BR-2302 | Beacon | IC- | BR-2302 | BR-2302 | MAC-2301 | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 5 | M20
109 | RD-1P-2-FA | MAC-2301 | Manual Call Point | IC- | MAC-2301 | MAC-2301 | FACP | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 100 | M20
110 | RD-1P-2-FA | HGD-2301 | Hydrogen Gas Detector | IC- | HGD-2301 | HGD-2301 | FACP | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 100 | M20
111 | RD-1P-2-F | FACP-DCS | FACP monitoring serial link | IC- | FACP-001 | FACP | DCS | FRS | - | NIS | 1 | Pair | 1.5 | Overal Screen | Red | Note 1 | 300/500 vac | 40 | M20
D01