## Cover
NISOC |  |  | افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
CABLE SCHEDULE FOR PAGA
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از5
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | TE | LI | 0004 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
CABLE SCHEDULE FOR PAGA نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | Feb .2023 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Sep .2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | June .2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 1 |  |  |  | Client Doc. Number: |  |  | F0Z-709094
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for Client Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوري بینک
CABLE SCHEDULE FOR PAGA
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | TE | LI | 0004 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | X | [5 empty] | 54
5 |  |  | X | [5 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LIST-Outdoor
|  |  | FROM |  |  | TO |  |  | SIGNAL | CABLE DETAIL
Item | Rev. | Cable Tag No. | EQUIPMENT TAG No. | LOCATION | EQUIPMENT DESCRIPTION | EQUIPMENT DESCRIPTION | LOCATION | CABLE CONNECTOR/ GLAND SIZE |  | SIZE | DESCRIPTION | ESTIMATED LENGTH (m) | DRUM
PAGA Power Cable Between NEW CONTROL BUILDING AND FIELD AEA
1 | D02 | BD-05-PA-RA-01 | PAGA-MDF-01 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | PA-ST-01 | Field Area | M25 | PAGA | 3 Core 4 mm2 | CU/PVC/XLPE/SWA/LC | 250
2 | D02 | BD-05-PA-RA-01 | PA-ST-01 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | PA-ST-02 | Field Area | M25 | PAGA | 3 Core 4 mm2 | CU/PVC/XLPE/SWA/LC | 100
3 | D02 | BD-05-PA-RA-01 | PAGA-MDF-01 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | PA-ST-03 | Field Area | M25 | PAGA | 3 Core 4 mm2 | CU/PVC/XLPE/SWA/LC | 400
4 | D02 | BD-05-PA-RA-02 | PA-ST-03 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | PA-ST-04 | Field Area | M25 | PAGA | 3 Core 4 mm2 | CU/PVC/XLPE/SWA/LC | 250
PAGA Power Cable Between Junction Box To Loudspeaker
5 | D02 | *-PA-SP-01-PC-1 | PA-ST-01 | Field Area | JUNCTION BOX | *-PA-SP-01 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
6 | D02 | *-PA-SP-02-PC-2 | PA-ST-01 | Field Area | JUNCTION BOX | *-PA-SP-02 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
7 | D02 | *-PA-SP-03-PC-3 | PA-ST-01 | Field Area | JUNCTION BOX | *-PA-SP-03 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
8 | D02 | *-PA-SP-04-PC-4 | PA-ST-01 | Field Area | JUNCTION BOX | *-PA-SP-04 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
9 | D02 | *-PA-SP-05-PC-5 | PA-ST-02 | Field Area | JUNCTION BOX | *-PA-SP-05 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
10 | D02 | *-PA-SP-06-PC-6 | PA-ST-02 | Field Area | JUNCTION BOX | *-PA-SP-06 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
11 | D02 | *-PA-SP-07-PC-7 | PA-ST-02 | Field Area | JUNCTION BOX | *-PA-SP-07 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
12 | D02 | *-PA-SP-08-PC-8 | PA-ST-02 | Field Area | JUNCTION BOX | *-PA-SP-08 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
13 | D02 | *-PA-SP-09-PC-9 | PA-ST-03 | Field Area | JUNCTION BOX | *-PA-SP-09 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
14 | D02 | *-PA-SP-10-PC-10 | PA-ST-03 | Field Area | JUNCTION BOX | *-PA-SP-10 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
15 | D02 | *-PA-SP-11-PC-11 | PA-ST-03 | Field Area | JUNCTION BOX | *-PA-SP-11 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
16 | D02 | *-PA-SP-12-PC-12 | PA-ST-03 | Field Area | JUNCTION BOX | *-PA-SP-12 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
17 | D02 | *-PA-SP-13-PC-13 | PA-ST-04 | Field Area | JUNCTION BOX | *-PA-SP-13 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
18 | D02 | *-PA-SP-14-PC-14 | PA-ST-04 | Field Area | JUNCTION BOX | *-PA-SP-14 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
19 | D02 | *-PA-SP-15-PC-15 | PA-ST-04 | Field Area | JUNCTION BOX | *-PA-SP-15 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
20 | D02 | *-PA-SP-16-PC-16 | PA-ST-04 | Field Area | JUNCTION BOX | *-PA-SP-16 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE | 5
POWER Cable Between UPS Distribution Panel AND Field Area(For Flasher of Loudspeaker)
21 | D01 |  | UPS | GCS Control Building(new) | ELEC PDP | *-PA-ST-01 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE/SWA/LC | 250
22 | D01 |  | UPS | GCS Control Building(new) | ELEC PDP | *-PA-ST-02 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE/SWA/LC | 350
23 | D01 |  | UPS | GCS Control Building(new) | ELEC PDP | *-PA-ST-03 | Field Area | M20 | PAGA | 3 Core 2.5 mm2 | CU/PVC/XLPE/SWA/LC | 450
Intercom Cable(Between New CCR & intercom set at field area)
24 | D01 | BD-05-PA-RA-01 | PAGA-MDF-01 | GCS Control Building(new) | INTERCOM MDF | *-PA-IC-01 | INTERCOM SET | M20 | SIGNAL | 4X2X0.8 mm | CU/PVC/(SC)/SWA/PVC/LC (OUTDOOR) | 500
25 | D01 | BD-05-PA-RA-02 | PAGA-MDF-02 | GCS Control Building(new) | INTERCOM MDF | *-PA-IC-02 | INTERCOM SET | M20 | SIGNAL | 4X2X0.8mm | CU/PVC/(SC)/SWA/PVC/LC (OUTDOOR) | 700
POWER Cable Between UPS Distribution Panel AND Field Area(For Flasher of INTERCOM SET)
26 | D01 | 1XL2 | UPS | GCS Control Building(new) | UPS Panel | INTERCOM FLASHER FOR INTERCM *-PA-IC-01 | INTERCOM FLASER | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/SWA/LC | 500
27 | D01 | 1XL2 | UPS | GCS Control Building(new) | UPS Panel | INTERCOM FLASHER FOR INTERCM 2 *-PA-IC-02 | INTERCOM FLASER | M20 | Power Cable | 3 Core 2.5 mm2 | CU/PVC/SWA/PVC/SWA/LC | 300
|  | LC:Lead Cover |  | NOTE : Loud speaker cable from JB will be routed to conduit & then connected to loudspeaker set
TC : Telephone Cable
PC : Power Cable
D02
تسهیلات
CABLE SCHEDULE FOR PAGA
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
TE
LI
0004
D02
بسته کاری
GCS
پروژه
BK

## LIST-Indoor
|  |  | FROM |  |  | TO |  |  | SIGNAL | CABLE DETAIL
Item | Rev. | Cable Tag No. | EQUIPMENT TAG No. | LOCATION | EQUIPMENT DESCRIPTION | EQUIPMENT DESCRIPTION | LOCATION | CABLE CONNECTOR/ GLAND SIZE |  | SIZE | DESCRIPTION | ESTIMATED LENGTH (m) | DRUM
PAGA Power Cable For Indoor Building
1 | D02 | CCR-LSP-01-PC-01 | PAGA -CCR-01 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | CCR-LSP-01 | AIR LOCK | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 20
2 | D02 | CCR-LSP-01-PC-02 | CCR-LSP-01 | NEW CONTROL BUILDING (Rack Room) | Ceiling Speaker | CCR-LSP-02 | CORRIDOR | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 15
3 | D02 | CCR-LSP-01-PC-03 | CCR-LSP-02 | NEW CONTROL BUILDING (Rack Room) | Ceiling Speaker | CCR-LSP-03 | CORRIDOR | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 10
4 | D02 | CCR-LSP-01-PC-04 | CCR-LSP-03 | NEW CONTROL BUILDING (Rack Room) | Ceiling Speaker | CCR-LSP-04 | CORRIDOR | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 15
5 | D02 | CCR-LSP-01-PC-05 | CCR-LSP-04 | NEW CONTROL BUILDING (Rack Room) | Ceiling Speaker | CCR-LSP-05 | CORRIDOR | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 10
6 | D02 | CCR-LSP-01-PC-06 | CCR-LSP-05 | NEW CONTROL BUILDING (Rack Room) | Ceiling Speaker | CCR-LSP-06 | CORRIDOR | M20 | PAGA | 3 Core 1.5 mm2 | CU/PVC/XLPE/LSZH | 20
7 | D03 | CCR-CO-01-T-01 | PAGA -CCR-01 | NEW CONTROL BUILDING (Rack Room) | PAGA MDF | PAGA CONSOLE | CCR | RJ45 | PAGA CONSOLE | CAT 6 | UTP(BY VENDOR) | 20
تسهیلات
CABLE SCHEDULE FOR PAGA
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
TE
LI
0004
D02
بسته کاری
GCS
پروژه
BK
D02