## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0030_D05 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1686 |  |  | Transmital Date: 11/Dec/2022
Document Title: Mechanical Data Sheets For Fire Water Main Pumps - Diesel Engine Driven |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-ME-TR-1686 |  |  | Transmital Date: 11/Dec/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0030_D04 |  |  | CRS Status:
item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| صفحه 11 از 30: همانگونه که در نامه شماره 367288 مورخ 1401/09/29 بیان گردید، ضروری است تعداد باتری های نیکل کادمیوم به دو مجموعه 20 تایی با ظرفیت حداقل 200 آمپر ساعت اصلاح گردد |  | 01/2294/412691 | 1401/10/29 | نقطه نظر کارفرمای محترم اعمال می گردد.
1 | تجهیزات ابزار دقیق مطابق استاندارد API 670 جهت دیزل پمپ آتش نشانی در نظر گرفته شود |  | 01/2294/412691 | 1401/10/29 | به اطلاع کارفرمای محترم می رساند مطابق مدارک مشخصات فنی پمپ های آتش نشانی و دیزل، کلیه تجهیزات ابزار دقیقی و کنترلی می بایست مطابق الزامات استاندارد NFPA 20 و IPS-M-PM-290 باشد که سازندگان ملزم به رعایت آن ها هستند همچنین با توجه به اینکه دیزل این پمپ ها با یک configuration ثابت از سازندگان خارجی تهیه می شود، اضافه نمودن تجهیزات کنترلی و ابزار دقیقی بر روی تجهیز مذکور شامل اثرات مالی و زمانی بوده و همچنین قابل پذیرش از طرف سازندگان دیزل نخواهد بود. بنابراین از دیدگاه این مشاور، الزامات پروژه در این خصوص کفایت کرده و نیازی به در نظر گرفتن ادوات ابزاردقیقی و کنترلی اضافه نمی باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
Date: 02/15/2023