## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CAUSE & EFFECT DIAGRAM
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 13
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | PR | CE | 0001 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
CAUSE & EFFECT DIAGRAM نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | FEB.2023 |  | IFA |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAY.2022 |  | IFC |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-708805
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CAUSE & EFFECT DIAGRAM
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 13
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | PR | CE | 0001 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | X | X | [6 empty] | 74
11 | X | X | [6 empty] | 75
12 | X | X | [6 empty] | 76
13 | X | X | [6 empty] | 77
14 | X | X | [6 empty] | 78
15 | X | X | [6 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Note
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CAUSE & EFFECT DIAGRAM
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از13
9184 – 073 - 053 | BK | GSC | PEDCO | 120 | PR | CE | 0001 | D01
NOTES | [9 empty] | Rev.
1- Following ESD levels are defined:
ESD 0: Total Plant Shutdown With Automatic Depressurizing
ESD 1A : Process Emergency ShutDown With Depressurizing
ESD 1: Process Emergency ShutDown Without Depressurizing
ESD2A :Train shut down With depressurizing
ESD 2: Train shut down Without depressurizing
ESD 3: Equipment shut down
2- All electrical source except essential power source shall be isolated.
3- Cause & Effect diagrams of packages will be prepared by vendors.
4-Definition of symbols:
A:Active
C: Close
O: Open / Start / On
S: Shut Down / Stop / Off
T: Trip
I:/Isolation
P: Permissive
PB:Push Button
R: Reset
V: Override
TD: Time Delay
5-Adjustable Delay
6-Time delay
REFERENCES | [9 empty] | D01
ESD Philosophy BK-GCS-PEDCO-120-PR-PH-0005 | [9 empty] | D01
Cause & Effect Diagram BK-GCS-PEDCO-120-PR-CE-0001 | [9 empty] | D01
ESD Block Diagram BK-GCS-PEDCO-120-PR-BD-0001 | [9 empty] | D01
ESD Level Hierarchy BK-GCS-PEDCO-120-IN-DG-0003 | [9 empty] | D01

## ESD -0
DESCRIPTION : ESD 0-Total Plant Shutdown With Automatic Depressurizing | [6 empty] | EFFECT | NOTE |  | (2) | (5 ,6)
[8 empty] | P&ID | - | - | - | -
[8 empty] | Equipment / Description | Total plant shut down | Emergency & Normal Power isolation which will trip all electrical sources | UPS Battery isolation by time delay. | Process Emergency ShutDown With Depressurizing
[8 empty] | TAG No. | ESD 0 |  |  | ESD-1A
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 | D01 | 0 | Manually from Central Control Room (CCR) | - |  | PB-2101 |  | 2 | A
2 |  | 0 | Confirmed Flammable Gas in HVAC air in-take (from F&G system) | - |  |  |  | 3 | A
3 |  | 1 | Network Power Failure |  |  |  |  | 6 | A
4 | D01 | 1 | PCS Failure |  |  |  |  | 7 | A
5 | D01 | 0 | UPS Failure | - |  |  |  | 4 | A
6 |  |  | Total Plant Shut Down With Automatic Depressurizing |  |  | ESD 0 |  | 5 |  | I | I | A
7 | [7 empty] | 6
8 | [7 empty] | 7
9 | [7 empty] | 8
10 | [7 empty] | 9
11 | [7 empty] | 10
12 | [7 empty] | 11
13 | [7 empty] | 12
14 | [7 empty] | 13
15 | [7 empty] | 14
16 | [7 empty] | 15
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 21
23 | [7 empty] | 22
24 | [7 empty] | 23
25 | [7 empty] | 24
26 | [7 empty] | 25
27 | [7 empty] | 26
28 | [7 empty] | 27
29 | [7 empty] | 28
30 | [7 empty] | 29
31 | [7 empty] | 30
32 | [7 empty] | 31
33 | [7 empty] | 32
34 | [7 empty] | 33
35 | [7 empty] | 34
36 | [7 empty] | 35
37 | [7 empty] | 36
38 | [7 empty] | 37
39 | [7 empty] | 38
40 | [7 empty] | 39
41 | [7 empty] | 40
42 | [7 empty] | 41
43 | [7 empty] | 42
44 | [7 empty] | 43
45 | [7 empty] | 44
46 | [7 empty] | 45
47 | [7 empty] | 46

## ESD -1A
DESCRIPTION : ESD 1A-Process Emergency ShutDown With Depressurizing | [6 empty] | EFFECT | NOTE | [7 empty] | D01 | D01
[8 empty] | P&ID | - | - |  | BK-GCS-PEDCO-120-PR-PI-0012 | BK-GCS-PEDCO-120-PR-PI-0013(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0005 | BK-GCS-PEDCO-120-PR-PI-0020 | BK-GCS-PEDCO-120-PR-PI-0017 (2/2)
[8 empty] | Equipment / Description | Process Emergency ShutDown With Depressurizing | Process Emergency ShutDown Without Depressurizing | Train shut down With depressurizing | Gas Compressor Discharge Drum Blow Down Valve( After ESDV's close confirmation) | Dehydration Package Blow Down Valve( After ESDV's close confirmation) | Power Isolation In Process Area | Inlet Knock Out Drum Blow Down Valve( by time delay) | Air Blower | Sump Pump
[8 empty] | TAG No. | ESD 1A | ESD 1 | ESD 2A | BDV-2141 | BDV-2151 | - | XV-2110 | FST-2201 | P-2203 A/B
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 0 | Total Plant Shut Down With Automatic Depressurizing | - |  | ESD-0 |  | 1 | A
2 |  | 1 | Process Emergency ShutDown Without Depressurizing(Activation of ESD-1 by time delay) | - |  | ESD-1 |  | 2 | A
3 |  | 1A | Confirmed Flammable Gas in fire zone (from F&G system) | - |  |  |  | 3 | A
4 | D01 |  | Deleted
5 | D01 | 1 | Instrument Air Heade Pressure Low Low (2 out of 3 voting) | BK-GCS-PEDCO-120-PR-PI-0015(2/2) |  | PALL-2201 A/B/C |  | 5 | A
6 | D01 | 1A | Manually from Central Control Room (CCR) by time delay |  |  | PB-2102 |  | 8 | A
7 |  | 1A | Process Emergency ShutDown With Depressurizing | - |  | ESD 1A |  | 10 |  | A | A | O | O | I | O | O | S
8
9 | [7 empty] | 11
10 | [7 empty] | 12
11 | [7 empty] | 13
12 | [7 empty] | 14
13 | [7 empty] | 15
14 | [7 empty] | 16
15 | [7 empty] | 17
16 | [7 empty] | 18
17 | [7 empty] | 19
18 | [7 empty] | 20
19 | [7 empty] | 21
20 | [7 empty] | 22
21 | [7 empty] | 23
22 | [7 empty] | 24
23 | [7 empty] | 25
24 | [7 empty] | 26
25 | [7 empty] | 27
26 | [7 empty] | 28
27 | [7 empty] | 29
28 | [7 empty] | 30
29 | [7 empty] | 31
30 | [7 empty] | 32
31 | [7 empty] | 33
32 | [7 empty] | 34
33 | [7 empty] | 35
34 | [7 empty] | 36
35 | [7 empty] | 37
36 | [7 empty] | 38
37 | [7 empty] | 39
38 | [7 empty] | 40
39 | [7 empty] | 41
40 | [7 empty] | 42
41 | [7 empty] | 43
42 | [7 empty] | 44
43 | [7 empty] | 45
44 | [7 empty] | 46

## ESD -1
DESCRIPTION : ESD 1- Process Emergency ShutDown Without Depressurizing | [6 empty] | EFFECT | NOTE |  | D01
[8 empty] | P&ID | - | - | - | - | BK-GCS-PEDCO-120-PR-PI-0018 | BK-GCS-PEDCO-120-PR-PI-0003 | BK-GCS-PEDCO-120-PR-PI-0002 | BK-GCS-PEDCO-120-PR-PI-0012
[8 empty] | Equipment / Description | Process Emergency ShutDown Without Depressurizing |  | Train shut down Without depressurizing | Equipment shut down | Corrosion Inhibitor Package | Golkhari Inlet Gas Pipeline Shut Down Valve | Binak Inlet Gas Pipeline Shut Down Valve | OUTLET GAS Compression Discharge Drum (V-2103)
[8 empty] | TAG No. | ESD 1 | Deleted | ESD 2 | ESD 3 | PK-2207 | ESDV-2102 | ESDV-2101 | ESDV-2142 ESDV-2143
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1A | Process Emergency ShutDown With Depressurizing | - |  | ESD 1A |  | 1 | A
2 |  | 1 | Push Button in CCR | - |  | PB-2103 |  | 2 | A
3 |  | 1 | Nitrogen Header Pressure Low Low | BK-GCS-PEDCO-120-PR-PI-0016 |  | PALL-2211 |  | 3 | A
4 | D01 |  | Deleted |  |  |  |  | 4
5 | D01 | 1 | Flare ignition failure |  |  |  |  | 5 | A
6 |  | 1 | PCS Failure |  |  |  |  | 6 | A
7 | D01 | 1 | High high Pressure pipe from sluge catcher to inlet K.O drum | BK-GCS-PEDCO-120-PR-PI-0005 |  | PIT-2116 |  | 7 | A
8 |  | 1 | High high liquid level inlet K.O drum | BK-GCS-PEDCO-120-PR-PI-0005 |  | LAHH-2117 |  | 8 | A
9 |  | 1 | Low Low Pressure Transfer Pipeline (Gas) | BK-GCS-PEDCO-120-PR-PI-0013(1/3) |  | PIT-2151 |  | 9 | A
10 |  | 1 | Flare K.O. Drum Level High High (2 out of 3 voting) | BK-GCS-PEDCO-120-PR-PI-0020(2/3) |  | LIA2252A/B/C |  | 10 | A
11 |  | 1 | High high pressure ( pipeline at inlet of sluge catcher drum) | BK-GCS-PEDCO-120-PR-PI-0004(1/2) |  | PIAHH-2111 |  | 11 | A
12 |  | 1 | High high liquid level Slug Catcher Drum | BK-GCS-PEDCO-120-PR-PI-0004(1/2) |  | LA-2112 |  | 12 | A
13 |  | 1 | High High liquid level in Gas Compression Discharge Drum | BK-GCS-PEDCO-120-PR-PI-0012 |  | LAHH-2142 |  | 13 | A
14 |  | 1 | DC charger failure |  |  |  |  | 14 | A
15 | D01 |  | Deleted |  |  |  |  | 15
16 |  | 1 | Process Emergency ShutDown Without Depressurizing |  |  |  |  | 16 | A |  | A | A | S/T | C | C | C
17 | [7 empty] | 17
18 | [7 empty] | 18
19 | [7 empty] | 19
19 | [7 empty] | 20
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 21
23 | [7 empty] | 22
24 | [7 empty] | 23
25 | [7 empty] | 24
26 | [7 empty] | 25
27 | [7 empty] | 26
28 | [7 empty] | 27
29 | [7 empty] | 28
30 | [7 empty] | 29
31 | [7 empty] | 30
32 | [7 empty] | 31
33 | [7 empty] | 32
34 | [7 empty] | 33
35 | [7 empty] | 34
36 | [7 empty] | 35
37 | [7 empty] | 36
38 | [7 empty] | 37
39 | [7 empty] | 38
40 | [7 empty] | 39
41 | [7 empty] | 40
42 | [7 empty] | 41
43 | [7 empty] | 42
44 | [7 empty] | 43
45 | [7 empty] | 44
46 | [7 empty] | 45
47 | [7 empty] | 1

## ESD -2A(TRAIN-A)
DESCRIPTION : ESD 2A- Train shut down With depressurizing(train A) | [6 empty] | EFFECT | NOTE |  |  |  |  | D01
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0009(1/3) | BK-GCS-PEDCO-120-PR-PI-0011 | BK-GCS-PEDCO-120-PR-PI-0007 (1/3)
[8 empty] | Equipment / Description | Train shut down With depressurizing (train A) | Train shut down Without depressurizing (train A) | 2Nd Stage Gas Compressor Suction Drum Blow Down Valve( After ESDV's close confirmation) | 2nd Satge Gas Compression Air Cooler Blow Down Valve(After ESDV's close confirmation) | 1st Stage Gas Compressor Train A
[8 empty] | TAG No. | ESD 2A | ESD2 | BDV-2134A | BDV-2132A | BDV-2121A
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1A | Process Emergency ShutDown With Depressurizing | - |  | ESD 1A |  | 1 | A
2 |  | 2 | Train shut down Without depressurizing (with time delay) | - | (Note 6) | ESD 2 |  | 2 | A
3 |  | 2A | Shut Down Push Button in CCR For Each Dedicated Train Of GCS | - |  | ESDR |  | 3 | A
4 |  | 2A | Confirm fire in process area |  |  |  |  | 7 | A
5 |  | 2A | Compressor failure signal form compressor package. (Depressurized Shutdown). | - |  |  |  | 5 | A
6 | D01 |  | Deleted
7 | D01 |  | Deleted
8 |  | 2A | Train A shutdown With Depressurizing | - |  | ESD 2A |  | 6 |  | A | O | O | O
9 | [7 empty] | 8
10 | [7 empty] | 9
11 | [7 empty] | 10
12 | [7 empty] | 11
13 | [7 empty] | 12
14 | [7 empty] | 13
15 | [7 empty] | 14
16 | [7 empty] | 15
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 21
23 | [7 empty] | 22
24 | [7 empty] | 23
25 | [7 empty] | 24
26 | [7 empty] | 25
27 | [7 empty] | 26
28 | [7 empty] | 27
29 | [7 empty] | 28
30 | [7 empty] | 29
31 | [7 empty] | 30
32 | [7 empty] | 31
33 | [7 empty] | 32
34 | [7 empty] | 33
35 | [7 empty] | 34
36 | [7 empty] | 35
37 | [7 empty] | 36
38 | [7 empty] | 37
39 | [7 empty] | 38
40 | [7 empty] | 39
41 | [7 empty] | 40
42 | [7 empty] | 41
43 | [7 empty] | 42
44 | [7 empty] | 43
45 | [7 empty] | 44
46 | [7 empty] | 45
47 | [7 empty] | 46
47

## ESD -2A(TRAIN-B)
DESCRIPTION : ESD 2A- Train shut down With depressurizing(train B) | [6 empty] | EFFECT | NOTE |  |  |  |  | D01
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0009(2/3) | BK-GCS-PEDCO-120-PR-PI-0011 (2/3) | BK-GCS-PEDCO-120-PR-PI-0007 (2/3)
[8 empty] | Equipment / Description | Train shut down With depressurizing(train A) | Train shut down Without depressurizing(train A) | 2Nd Stage Gas Compressor Suction Drum Blow Down Valve( After ESDV's close confirmation) | 2nd Satge Gas Compression Air Cooler Blow Down Valve(After ESDV's close confirmation) | 1st Stage Gas Compressor Train B
[8 empty] | TAG No. | ESD 2A | ESD2 | BDV-2134 B | BDV-2132 B | BDV-2121B
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1A | Process Emergency ShutDown With Depressurizing | - |  | ESD 1A |  | 1 | A
2 |  | 2 | Train shut down Without depressurizing (with time delay) | - | (Note 6) | ESD 2 |  | 2 | A
3 |  | 2A | Shut Down Push Button in CCR For Each Dedicated Train Of GCS | - |  | ESDR |  | 3 | A
7 |  | 2A | Confirm fire in process area |  |  |  |  | 7 | A
6 | D01 |  | Deleted
7 | D01 |  | Deleted
8 |  | 2A | Train A shutdown With Depressurizing | - |  | ESD 2A |  | 6 |  | A | O | O | O
9 | [7 empty] | 8
10 | [7 empty] | 9
11 | [7 empty] | 10
12 | [7 empty] | 11
13 | [7 empty] | 12
14 | [7 empty] | 13
15 | [7 empty] | 14
16 | [7 empty] | 15
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 21
22 | [7 empty] | 22
23 | [7 empty] | 23
24 | [7 empty] | 24
25 | [7 empty] | 25
26 | [7 empty] | 26
27 | [7 empty] | 27
28 | [7 empty] | 28
29 | [7 empty] | 29
30 | [7 empty] | 30
31 | [7 empty] | 31
32 | [7 empty] | 32
33 | [7 empty] | 33
34 | [7 empty] | 34
35 | [7 empty] | 35
36 | [7 empty] | 36
37 | [7 empty] | 37
38 | [7 empty] | 38
39 | [7 empty] | 39
40 | [7 empty] | 40
41 | [7 empty] | 41
42 | [7 empty] | 42
43 | [7 empty] | 43
44 | [7 empty] | 44
45 | [7 empty] | 45
46 | [7 empty] | 46
47

## ESD -2A(TRAIN-C)
DESCRIPTION : ESD 2A- Train shut down With depressurizing (Train C) | [6 empty] | EFFECT | [6 empty] | D01
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0009 (3/3) | BK-GCS-PEDCO-120-PR-PI-0011 (3/3) | MIAS-06-HE_120-PR-PI-0011 | BK-GCS-PEDCO-120-PR-PI-0007 (3/3)
[8 empty] | Equipment / Description | Train shut down With depressurizing (Train C) | Train shut down Without depressurizing (Train C) | 2Nd Stage Gas Compressor Suction Drum Blow Down Valve( After ESDV's close confirmation) | 2nd Satge Gas Compression Air Cooler Blow Down Valve(After ESDV's close confirmation) | 1st Stage compressor Blow Down Valve(BY time delay) | 1st Stage Gas Compressor train C
[8 empty] | TAG No. | ESD 2A | ESD2 | BDV-2134 C | BDV-2132 C | BDV-1013D | BDV-2121C
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1A | Process Emergency ShutDown With Depressurizing | - |  | ESD 1A |  | 1 | A
2 |  | 2 | Train shut down Without depressurizing (with time delay) | - | (Note 6) | ESD 2 |  | 2 | A
3 |  | 2A | Shut Down Push Button in CCR For Each Dedicated Train Of GCS | - |  | ESDR |  | 3 | A
4 |  | 2A | Confirm fire in process area |  |  |  |  | 7 | A
5 | D01 |  | Deleted
6 | D01 |  | Deleted
7 |  | 2A | Train C shutdown With Depressurizing | - |  | ESD 2A |  | 6 |  | A | O | O | C | O
8 | [7 empty] | 9
9 | [7 empty] | 10
10 | [7 empty] | 11
11 | [7 empty] | 12
12 | [7 empty] | 13
13 | [7 empty] | 14
14 | [7 empty] | 15
15 | [7 empty] | 16
16 | [7 empty] | 17
17 | [7 empty] | 18
18 | [7 empty] | 19
19 | [7 empty] | 20
20 | [7 empty] | 21
21 | [7 empty] | 22
22 | [7 empty] | 23
23 | [7 empty] | 24
24 | [7 empty] | 25
25 | [7 empty] | 26
26 | [7 empty] | 27
27 | [7 empty] | 28
28 | [7 empty] | 29
29 | [7 empty] | 30
30 | [7 empty] | 31
31 | [7 empty] | 32
32 | [7 empty] | 33
33 | [7 empty] | 34
34 | [7 empty] | 35
35 | [7 empty] | 36
36 | [7 empty] | 37
37 | [7 empty] | 38
38 | [7 empty] | 39
39 | [7 empty] | 40
40 | [7 empty] | 41
41 | [7 empty] | 42
42 | [7 empty] | 43
43 | [7 empty] | 44
44 | [7 empty] | 45
45 | [7 empty] | 46

## ESD -2(TRAIN-A)
DESCRIPTION : ESD 2- Train shut down Without depressurizing (Train A) | [6 empty] | EFFECT | NOTE
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0006(1/3) | BK-GCS-PEDCO-120-PR-PI-0011(1/3) | BK-GCS-PEDCO-120-PR-PI-000 7(1/3) | BK-GCS-PEDCO-120-PR-PI-0010(1/3)
[8 empty] | Equipment / Description | Train shut down Without depressurizing (Train A) | Train shut down With depressurizing (Train A) | Inlet 1st Stage Compressor 1st Stage Gas Compression Suction Drum (Train A) | outlet On/Off Valve 2nd Stage Gas Compressor Air Cooler (Train A) | 1st stage gas compressor (Train A) | 2nd stage gas compressor (Train A)
[8 empty] | TAG No. | ESD 2 | ESD2A | XV-2121A | XV-2133A | C-2101A | C-2102A
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1 | Process Emergency ShutDown Without Depressurizing | - |  | ESD 1 |  | 1 | A
2 |  | 2A | Train shut down With depressurizing(Train A) | - |  | ESD 2A |  | 2 | A
3 |  | 2 | Compressor failure signal form compressor package (Pressurized Shutdown). | - |  |  |  | 3 | A
4 |  | 2 | High High level in 1st Stage Gas Compression Suction Drum Train A | BK-GCS-PEDCO-120-PR-PI-0006(1/3) |  | LIAHH-2122 |  | 4 | A
5 |  | 2 | Low Low peressure in suction of 1st Stage Gas Compressor Train A | BK-GCS-PEDCO-120-PR-PI-0007(1/3) |  | PIA -2122A |  | 6 | A
6 |  | 2 | Low Low pressure in suction of 2nd Stage Gas Compressor Train A | BK-GCS-PEDCO-120-PR-PI-0010(1/3) |  | PIA-2132B |  | 7 | A
7 |  | 2 | High High Pressure in suction of 1ST Stage compressor Train A | BK-GCS-PEDCO-120-PR-PI-0007(1/3) |  | PIA-2122A |  | 8 | A
8 |  | 2 | High High Pressure in discharge of 1st Stage compressor Train A | BK-GCS-PEDCO-120-PR-PI-0007(1/3) |  | PIA-2125A |  | 9 | A
9 |  | 2 | High High Pressure in discharge of 2nd Stage compressor Train A | BK-GCS-PEDCO-120-PR-PI-0010(1/3) |  | PIA-2134B |  | 10 | A
10 |  | 2 | High High Temprature in dischage of 1st Stage compressor Train A | BK-GCS-PEDCO-120-PR-PI-0007(1/3) |  | TIAHH-2124A |  | 11 | A
11 |  | 2 | High High level in 2nd Stage Gas Compression Suction Drum Train A | BK-GCS-PEDCO-120-PR-PI-0009(1/3) |  | LIAHH-2132B |  | 5 | A
12 |  | 2 | High High Temprature in dischage of 2nd Stage compressor train A | BK-GCS-PEDCO-120-PR-PI-0010(1/3) |  | TIAHH-2134B |  | 12 | A
13 |  | 2 | Shut down push button in CCR for dedicated GCS Train A |  |  | ESDR |  | 13 | A
14 |  | 2 | High High Temprature in dischage of 1st Stage gas compressor air cooler Train A | BK-GCS-PEDCO-120-PR-PI-0008(1/3) |  | TIAHH-2125A |  | 14 | A
15 |  | 2 | High High Temprature in dischage of 2nd Stage gas compressor air cooler Train A | BK-GCS-PEDCO-120-PR-PI-0011(1/3) |  | TIAHH-2136A
16 |  | 2 | Train shut down Without depressurizing (Train A) |  |  | ESD 2 |  | 15 |  | A(6) | C | C | T | T
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 24
23 | [7 empty] | 25
24 | [7 empty] | 26
25 | [7 empty] | 27
26 | [7 empty] | 28
27 | [7 empty] | 29
28 | [7 empty] | 30
29 | [7 empty] | 31
30 | [7 empty] | 32
31 | [7 empty] | 33
32 | [7 empty] | 34
33 | [7 empty] | 35
34 | [7 empty] | 36
35 | [7 empty] | 37
36 | [7 empty] | 38
37 | [7 empty] | 39
38 | [7 empty] | 40
39 | [7 empty] | 41
40 | [7 empty] | 42
41 | [7 empty] | 43
42 | [7 empty] | 44
43 | [7 empty] | 45
44 | [7 empty] | 46

## ESD -2(TRAIN-B)
DESCRIPTION : ESD 2- Train shut down Without depressurizing (Train B) | [6 empty] | EFFECT | NOTE
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0006(2/3) | BK-GCS-PEDCO-120-PR-PI-0011(2/3) | BK-GCS-PEDCO-120-PR-PI-0007(2/3) | BK-GCS-PEDCO-120-PR-PI-0010(2/3)
[8 empty] | Equipment / Description | Train shut down Without depressurizing (Train B) | Equipmen shutdown (Train B) | Inlet 1st Stage Compressor 1st Stage Gas Compression Suction Drum (Train B) | outlet On/Off Valve 2nd Stage Gas Compressor Air Cooler (Train B) | 1st stage gas compressor (Train B) | 2nd stage gas compressor (Train B)
[8 empty] | TAG No. | ESD 2 | ESD 3 | XV-2121B | XV-2133B | C-2101B | C-2102B
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1 | Process Emergency ShutDown Without Depressurizing | - |  | ESD 1 |  | 1 | A
2 |  | 2A | Train shut down With depressurizing (Train B) | - |  | ESD 2A |  | 2 | A
3 |  | 2 | Compressor failure signal form compressor package (Pressurized Shutdown). | - |  |  |  | 3 | A
4 |  | 2 | High High level in train A 1st Stage Gas Compression Suction Drum (Train B) | BK-GCS-PEDCO-120-PR-PI-0006(2/3) |  | LIAHH-2122A |  | 4 | A
5 |  | 2 | Low Low peressure in suction of 1st Stage Gas Compressor Train B | BK-GCS-PEDCO-120-PR-PI-0007(2/3) |  | PIA-2122A |  | 6 | A
6 |  | 2 | Low Low pressure in suction of 2nd Stage Gas Compressor Train B | BK-GCS-PEDCO-120-PR-PI-0010(2/3) |  | PIA-2132B |  | 7 | A
7 |  | 2 | High High Pressure in suction of 1ST Stage compressor (Train B) | BK-GCS-PEDCO-120-PR-PI-0007(2/3) |  | PIA-2122A |  | 8 | A
8 |  | 2 | High High Pressure in discharge of 1st Stage compressor (Train B) | BK-GCS-PEDCO-120-PR-PI-0007(2/3) |  | PIA-2125A |  | 9 | A
9 |  | 2 | High High Pressure in discharge of 2nd Stage compressor (Train B) | BK-GCS-PEDCO-120-PR-PI-0010(2/3) |  | PIA-2134B |  | 10 | A
10 |  | 2 | High High Temprature in dischage of 1st Stage compressor (Train B) | BK-GCS-PEDCO-120-PR-PI-0007(2/3) |  | TIAHH-2124A |  | 11 | A
11 |  | 2 | High High level in train A 2nd Stage Gas Compression Suction Drum (Train B) | BK-GCS-PEDCO-120-PR-PI-0009(2/3) |  | LIAHH-2132B |  | 5 | A
12 |  | 2 | High High Temprature in dischage of 2nd Stage compressor (Train B) | BK-GCS-PEDCO-120-PR-PI-0010(2/3) |  | TIAHH-2134B |  | 12 | A
13 |  | 2 | Shut down push button in CCR for dedicated GCS (Train B) |  |  | ESDR |  | 13 | A
14 |  | 2 | High High Temprature in dischage of 1st Stage gas compressor air cooler (Train B) | BK-GCS-PEDCO-120-PR-PI-0008(2/3) |  | TIAHH-2125A |  | 14 | A
15 |  | 2 | High High Temprature in dischage of 2nd Stage gas compressor air cooler (Train B) | BK-GCS-PEDCO-120-PR-PI-0011(2/3) |  | TIAHH-2136A
16 |  | 2 | Train shut down Without depressurizing (Train B) |  |  | ESD 2 |  | 15 |  | A | C | C | T | T
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 21
23 | [7 empty] | 24
24 | [7 empty] | 25
25 | [7 empty] | 26
26 | [7 empty] | 27
27 | [7 empty] | 28
28 | [7 empty] | 29
29 | [7 empty] | 30
30 | [7 empty] | 31
31 | [7 empty] | 32
32 | [7 empty] | 33
33 | [7 empty] | 34
34 | [7 empty] | 35
35 | [7 empty] | 36
36 | [7 empty] | 37
37 | [7 empty] | 38
38 | [7 empty] | 39
39 | [7 empty] | 40
40 | [7 empty] | 41
41 | [7 empty] | 42
42 | [7 empty] | 43
43 | [7 empty] | 44
44 | [7 empty] | 45
45 | [7 empty] | 46

## ESD -2(TRAIN-C)
DESCRIPTION : ESD 2- Train shut down Without depressurizing (Train C) | [6 empty] | EFFECT | NOTE
[8 empty] | P&ID | - | - | BK-GCS-PEDCO-120-PR-PI-0006(3/3) | BK-GCS-PEDCO-120-PR-PI-0011(1/3) | BK-GCS-PEDCO-120-PR-PI-0007(3/3) | BK-GCS-PEDCO-120-PR-PI-0010(3/3)
[8 empty] | Equipment / Description | Train shut down Without depressurizing(train C) | Equipmen shutdown(train C) | Inlet 1st Stage Compressor 1st Stage Gas Compression Suction Drum Train A | outlet On/Off Valve 2nd Stage Gas Compressor Air Cooler train C | 1st stage gas compressor(Train C) | 2nd stage gas compressor (Train C)
[8 empty] | TAG No. | ESD 2 | ESD 3 | XV-2121C | XV-2133C | C-2101C | C-2102C
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1 | Process Emergency ShutDown Without Depressurizing | - |  | ESD 1 |  | 1 | A
2 |  | 2A | Train shut down With depressurizing(Train C) | - |  | ESD 2A |  | 2 | A
3 |  | 2 | Compressor failure signal form compressor package (Pressurized Shutdown). | - |  |  |  | 3 | A
4 |  | 2 | High High level in 1st Stage Gas Compression Suction Drum Train C | BK-GCS-PEDCO-120-PR-PI-0006(3/3) |  | LIAHH-2122A |  | 4 | A
5 |  | 2 | Low Low peressure in suction of 1st Stage Gas Compressor Train C | BK-GCS-PEDCO-120-PR-PI-0007(3/3) |  | PIA-2122A |  | 6 | A
6 |  | 2 | Low Low pressure in suction of 2nd Stage Gas Compressor Train C | BK-GCS-PEDCO-120-PR-PI-0010(3/3) |  | PIA-2132B |  | 7 | A
7 |  | 2 | High High Pressure in suction of 1ST Stage compressor Train C | BK-GCS-PEDCO-120-PR-PI-0007(3/3) |  | PIA-2122A |  | 8 | A
8 |  | 2 | High High Pressure in discharge of 1st Stage compressor Train C | BK-GCS-PEDCO-120-PR-PI-0007(3/3) |  | PIA-2125A |  | 9 | A
9 |  | 2 | High High level in 2nd Stage Gas Compression Suction Drum Train C | BK-GCS-PEDCO-120-PR-PI-0009(3/3) |  | LIAHH-2132B |  | 5 | A
10 |  | 2 | High High Pressure in discharge of 2nd Stage compressor Train C | BK-GCS-PEDCO-120-PR-PI-0010(3/3) |  | PIA-2134B |  | 10 | A
11 |  | 2 | High High Temprature in dischage of 1st Stage compressor Train C | BK-GCS-PEDCO-120-PR-PI-0007(3/3) |  | TIAHH-2124A |  | 11 | A
12 |  | 2 | High High Temprature in dischage of 2nd Stage compressor Train C | BK-GCS-PEDCO-120-PR-PI-0010(3/3) |  | TIAHH-2134B |  | 12 | A
13 |  | 2 | Shut down push button in CCR for dedicated GCS Train C |  |  | ESDR |  | 13 | A
14 |  | 2 | High High Temprature in dischage of 1st Stage gas compressor air cooler Train C | BK-GCS-PEDCO-120-PR-PI-0008(3/3) |  | TIAHH-2125A |  | 14 | A
15 |  | 2 | High High Temprature in dischage of 2nd Stage gas compressor air cooler Train C | BK-GCS-PEDCO-120-PR-PI-0011(3/3) |  | TIAHH-2136A
16 |  | 2 | Train shut down Without depressurizing(Train C) |  |  | ESD 2 |  | 15 |  | A | C | C | T | T
17 | [7 empty] | 16
18 | [7 empty] | 17
19 | [7 empty] | 18
20 | [7 empty] | 19
21 | [7 empty] | 20
22 | [7 empty] | 21
23 | [7 empty] | 24
24 | [7 empty] | 25
25 | [7 empty] | 26
26 | [7 empty] | 27
27 | [7 empty] | 28
28 | [7 empty] | 29
29 | [7 empty] | 30
30 | [7 empty] | 31
31 | [7 empty] | 32
32 | [7 empty] | 33
33 | [7 empty] | 34
34 | [7 empty] | 35
35 | [7 empty] | 36
36 | [7 empty] | 37
37 | [7 empty] | 38
38 | [7 empty] | 39
39 | [7 empty] | 40
40 | [7 empty] | 41
41 | [7 empty] | 42
42 | [7 empty] | 43
43 | [7 empty] | 44
44 | [7 empty] | 45
45 | [7 empty] | 46

## ESD -3
DESCRIPTION : ESD 3-EQUIPMENT SHUT DOWN | [6 empty] | EFFECT | NOTE | [13 empty] | D01 | D01 | D01 | D01 | D01 | D01 | D01 | D01 | [16 empty] | D01 | D01
[8 empty] | P&ID | - | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005 |  | BK-GCS-PEDCO-120-PR-PI-0006(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0009(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0006(2/3) |  | BK-GCS-PEDCO-120-PR-PI-0009(2/3) |  | BK-GCS-PEDCO-120-PR-PI-0006(3/3) |  | BK-GCS-PEDCO-120-PR-PI-0009(3/3) |  | BK-GCS-PEDCO-120-PR-PI-0008(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0008(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0011(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0011(1/3) |  | BK-GCS-PEDCO-120-PR-PI-0012 |  | BK-GCS-PEDCO-120-PR-PI-0014 |  | BK-GCS-PEDCO-120-PR-PI-0015(1/2) |  | BK-GCS-PEDCO-120-PR-PI-0017(2/2) |  | BK-GCS-PEDCO-120-PR-PI-0019 |  | BK-GCS-PEDCO-120-PR-PI-0020(2/3) |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | BK-GCS-PEDCO-120-PR-PI-0022 |  | BK-GCS-PEDCO-120-PR-PI-0023
[8 empty] | Equipment / Description | Equipment shut down | [6 empty] | Equipment shut down train | V-2105 liquid outlet ESDV valve | Equipment shut down | V-2101A liquid outlet ON/OFF valve | Equipment shut down | V-2102A liquid outlet ON/OFF valve | Equipment shut down | V-2101A liquid outlet ON/OFF valve | Equipment shut down | V-2102A liquid outlet ON/OFF valve | Equipment shut down | V-2101A liquid outlet ON/OFF valve | Equipment shut down | V-2102A liquid outlet ON/OFF valve | Equipment shut down AE-2101-M1 | 1st stage gas air cooler trainA-Motor1 | Equipment shut down AE-2101-M2 | 1st stage gas air cooler trainA-Motor2 | Equipment shut down AE-2102-M1 | 2nd stage gas air cooler trainA-Motor1 | Equipment shut down AE-2102-M1 | 2nd stage gas air cooler trainA-Motor2 | Equipment shut down V-2103 | Liquid Outlet Gas Compessin Discharge Drum On/Off Valve | Equipment shut down Glycol Transfer Pump | Glycol Transfer Pump | Equipment shut down | Gas Outlet Of PK-C-2203 A/B ESDV Valve (To Plant Air) | Equipment shut down P-2202A/B | Close Drain Drum Pump |  |  | Equipment shut down | Lp Flare K.O.Drum Pump | Equipment shut down | Fuel Gas K.O. Drum (Inlet Line) | Equipment shut down XV Valve | Fuel Gas K.O. Drum | Equipment shut down P-2206 | Diesel Pump
[8 empty] | TAG No. | ESD 3 | ESD 3 | P-2101A | ESD 3 | P-2101B | ESD 3 | P-2101A | ESD 3 | ESDV-2113 | ESD 3 | XV-2122A | ESD 3 | XV-2131A | ESD 3 | XV-2122B | ESD 3 | XV-2131B | ESD 3 | XV-2122C | ESD 3 | XV-2131C | ESD 3 | AE-2101-M1 | ESD 3 | AE-2101-M2 | ESD 3 | AE-2102-M1 | ESD 3 | AE-2102-M2 | ESD 3 | XV-2144 | ESD 3 | P-2103 A/B | ESD 3 | ESDV-2201 | ESD 3 | P-2202 A/B | DELETED | DELETED | ESD 3 | P-2201 A/B | ESD 3 | ESDV-2272 | ESD 3 | XV-2271 | ESD 3 | P-2206
CAUSE
No | Rev. | Level | DESCRIPTION | P & ID | Note | TAG No. |  | No
1 |  | 1 | Process Emergency ShutDown Without Depressurizing | - |  | ESD 1 |  | 1 | A
2 |  | 2 | Train shut down Without depressurizing | - |  | ESD 2 |  | 2 | A
3 | D01 | 3 | High high pressure at discharge pump-2101 A | BK-GCS-PEDCO-120-PR-PI-0004 |  | PA-2116A |  | 3 |  | A
4 | D01 | 3 | Equipment Shut Down P-2101 |  |  | ESD3 |  | 4 |  |  | T
5 | D01 | 3 | High high pressure at discharge pump-2101 B | BK-GCS-PEDCO-120-PR-PI-0004 |  | PA-2116B |  | 5 |  |  |  | A
6 | D01 | 3 | Equipment Shut Down P-2101 |  |  | ESD3 |  | 6 |  |  |  |  | T
7 | D01 | 3 | Low Low pressure at suction pump-2101 A | BK-GCS-PEDCO-120-PR-PI-0004 |  | PA-2114A | [5 empty] | A
8 | D01 | 3 | Equipment Shut Down P-2101 |  |  | ESD3 | [6 empty] | T
9 | D01 | 3 | Low Low pressure at suction pump-2101 B | BK-GCS-PEDCO-120-PR-PI-0004 |  | PA-2114B | [5 empty] | A
10 | D01 | 3 | Equipment Shut Down P-2101 |  |  | ESD3 | [6 empty] | T
11 | D01 | 3 | Low low pressure at condenste pipe line | BK-GCS-PEDCO-120-PR-PI-0004 |  | PIA-2115 |  | 7 | [5 empty] | A
12 | D01 | 3 | Equipment Shut Down P-2101 |  |  | ESD3 |  | 8 | [6 empty] | T
13 |  | 3 | Low Low liquid level inlet K.O drum | BK-GCS-PEDCO-120-PR-PI-0005 |  | LALL-2118 |  | 9 | [7 empty] | A
14 |  | 3 | Equipment Shut Down V-2105 |  |  | ESD 3 |  | 10 | [8 empty] | C
15 |  | 3 | Low Low Liquid level at 1st Stage Gas Compression Suction Drum Train A | BK-GCS-PEDCO-120-PR-PI-0006(1/3) |  | LA-2122A |  | 11 | [9 empty] | A
16 |  | 3 | Equipment Shut Down V-2101 A |  |  | ESD 3 |  | 12 | [10 empty] | C
17 |  | 3 | Low Low level in train A 2nd Stage Gas Compression Suction Drum Train A | BK-GCS-PEDCO-120-PR-PI-0009(1/3) |  | LALL-2132B |  | 13 | [11 empty] | A
18 |  | 2 | Equipment Shut Down V-2101 A |  |  | ESD 3 |  | 14 | [12 empty] | C
19 | D01 | 3 | Low Low Liquid level at 1st Stage Gas Compression Suction Drum Train B | BK-GCS-PEDCO-120-PR-PI-0006(1/3) |  | LA-2122A |  | 15 | [13 empty] | A
20 | D01 | 3 | Equipment Shut Down V-2101 B |  |  | ESD 3 |  | 16 | [14 empty] | C
21 | D01 | 3 | Low Low level in train A 2nd Stage Gas Compression Suction Drum Train B | BK-GCS-PEDCO-120-PR-PI-0009(1/3) |  | LALL-2132B |  | 17 | [15 empty] | A
22 | D01 | 2 | Equipment Shut Down V-2101 B |  |  | ESD 3 |  | 18 | [16 empty] | C
23 | D01 | 3 | Low Low Liquid level at 1st Stage Gas Compression Suction Drum Train C | BK-GCS-PEDCO-120-PR-PI-0006(1/3) |  | LA-2122A |  | 19 | [17 empty] | A
24 | D01 | 3 | Equipment Shut Down V-2101 C |  |  | ESD 3 |  | 20 | [18 empty] | C
25 | D01 | 3 | Low Low level in train A 2nd Stage Gas Compression Suction Drum Train C | BK-GCS-PEDCO-120-PR-PI-0009(1/3) |  | LALL-2132B |  | 21 | [19 empty] | A
26 | D01 | 2 | Equipment Shut Down V-2101 C |  |  | ESD 3 |  | 22 | [20 empty] | C
27 |  | 3 | High motor vibration AE-2101A-M1 | BK-GCS-PEDCO-120-PR-PI-0008(1/3) |  | VSHH-2121 A |  | 23 | [21 empty] | A
28 |  | 3 | Equipment Shut Down AE-2101-M1 |  |  | ESD 3 |  | 24 | [22 empty] | T
29 |  | 3 | High motor vibration AE-2101A-M2 | BK-GCS-PEDCO-120-PR-PI-0008(1/3) |  | VSHH-2122A |  | 25 | [23 empty] | A
30 |  | 3 | Equipment Shut Down AE-2101-M2 |  |  | ESD 3 |  | 26 | [24 empty] | T
31 |  | 3 | High motor vibration AE-2102A-M1 | BK-GCS-PEDCO-120-PR-PI-0011(1/3) |  | VSHH-2131 A |  | 27 | [25 empty] | A
32 |  | 3 | Equipment Shut Down AE-2102-M1 |  |  | ESD 3 |  | 28 | [26 empty] | T
33 |  | 3 | High motor vibration AE-2102-M2 | BK-GCS-PEDCO-120-PR-PI-0011(1/3) |  | VSHH-2132 A |  | 29 | [27 empty] | A
34 |  | 3 | Equipment Shut Down AE-2102-M2 |  |  | ESD 3 |  | 30 | [28 empty] | T
35 |  | 3 | Low Low level in Gas Compression Discharge Drum | BK-GCS-PEDCO-120-PR-PI-0012 |  | LALL2142 |  | 31 | [29 empty] | A
36 |  | 3 | Equipment Shut Down V-2103 |  |  | ESD 3 |  | 32 | [30 empty] | C
37 |  | 3 | Low Low Liquid Level Of Lean Glaycol Storage Tank TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 |  | LALL-2161 |  | 33 | [31 empty] | A
38 |  | 3 | Equipment Shut Down P-2103 |  |  | ESD 3 |  | 34 | [32 empty] | S
39 |  | 3 | Low Low Pressure Outlet of Air Compressor Package PK-C-2203 A/B | BK-GCS-PEDCO-120-PR-PI-0015(1/2) |  | PIALL-2202 |  | 35 | [33 empty] | A
40 |  | 3 | Equipment Shut Down P-2103 |  |  |  |  | 36 | [34 empty] | C
41 |  | 3 | Low Low Liquid Level Close Drain Drum V-2202 | BK-GCS-PEDCO-120-PR-PI-0017(2/2) |  | LALL-2222 |  | 37 | [35 empty] | A
42 |  | 3 | Equipment Shut Down P-2202 |  |  | ESD3 |  | 38 | [36 empty] | S
43 | D01 | 3 | DELETED |  |  |  |  | 39
44 | D01 | 3 | DELETED |  |  |  |  | 40
45 |  | 3 | Low Low Liquid Level in Lp Flare K.O. Drum | BK-GCS-PEDCO-120-PR-PI-0020(2/3) |  | LIALL-2253 |  | 41 | [39 empty] | A
46 |  | 3 | Equipment Shut Down P-2201A/B |  |  | ESD3 |  | 42 | [40 empty] | S
47 | D01 | 3 | High high Liquid Level in Fuel Gas K.O. Drum | BK-GCS-PEDCO-120-PR-PI-0022 |  | LICAHH-2272 |  | 43 | [41 empty] | A
48 |  | 3 | Equipment Shut Down ESDV-2272 |  |  | ESD3 |  | 44 | [42 empty] | C
49 |  | 3 | Low Low Liquid Level in Fuel Gas K.O. Drum | BK-GCS-PEDCO-120-PR-PI-0022 |  | LICALL-2272 |  | 45 | [43 empty] | A
50 |  | 3 | Equipment Shut Down XV-2271 |  |  | ESD3 |  | 46 | [44 empty] | C
51 | D01 | 3 | Deleted |  |  |  |  | 47
52 | D01 | 3 | Deleted |  |  |  |  | 48