## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-MR-0006_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1573 |  |  | Transmital Date: 05/Nov/2022
Document Title: PMR For Instrument/Plant Air & Nitrogen Packages |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0110-ME-TR-1573 |  |  | Transmital Date: 05/Nov/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-MR-0006_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سیستم های کنترل کمپرسورهای هوا مستقل از درایرها می باشند. درایرها هر کدام پنل کنترلی مجزا داشته باشند. هر کمپرسور هوا یک پنل (PLC-Based) مجزا دارد که در ساختمان کنترل قرار دارد. نوت 10 نقشه P&ID پیوست (BK-GCS-PEDCO-120-PR-PI-0015_D04) صحیح نمی باشد. (حذف گردد) پنل UCP(PLC based) مربوط به پکیج نیتروژن در ساختمان کنترل در نظر گرفته شود. |  | 01/2294/391228 | 1401/10/14 | مطابق اسناد پایه سیستم های کنترلی کمپرسورهای هوا و پکیج نیتروژن بصورت PLC based و مستقل از درایرها در اتاق کنترل در نظر گرفته شده اند که در مدارک مشخصات فنی اصلاح شده کمپرسور هوا و درایرها به پیوست MR خدمت کارفرمای محترم ارائه می گردد. نقشه P&ID به شماره "BK-GCS-PEDCO-120-PR-PI-0015_D04" در ویرایش بعدی اصلاح و به پیوست مدرک MR خدمت کارفرمای محترم ارسال خواهد گردید. (آخرین ویرایش مدارک پیوست MR جهت استحضار و بررسی کارفرمای محترم ارسال می گردد.)
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: |  |  |  |  | Date: 02/19/2023