## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1547 |  |  | Transmital Date: 25-Oct-2022
Document Title: Earthing & Lightning Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0108-EL-TR-1547 |  |  | Transmital Date: 25-Oct-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نحوه اتصال کابل ارت به میله های دارای چاله بازدید از طریق کلمپ و برای میله های بدون چاله بازدید به صورت Cad Weld نمایش داده شود. |  | 1401-2294-315872 | 1401-08-26 | مطابق با مدرک "Typical Installation Details & Notes for Earthing and Lightning Protection System" نحوه اتصال کابل ارت به میله راد هم در چاله های بازدید و هم غیر از آن به صورت کلمپ خواهد بود که به E.S.1 نیز اشاره شده است.
2 | صفحه 2 از 7، تعداد چاله های ارت به 3 عدد افزایش یابد. |  | 1401-2294-315872 | 1401-08-26 | اعمال گردید.
3 | صفحه 3 از 7 جهت سیستم ارت حفاظتی اتاق CCTV یک عدد میله ارت با چاله بازدید لحاظ گردد و سپس به شبکه ارت موجود اتصال یابد. |  | 1401-2294-315872 | 1401-08-26 | اعمال گردید.
4 | صفحه 4 از 7 حداقل جهت 2 عدد از میله های ارت چاله بازدید در نظر گرفته شود. |  | 1401-2294-315872 | 1401-08-26 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Nov-22 |  |  |  |  | Date: