## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1547 |  |  | Transmital Date: 25-Oct-2022
Document Title: Earthing & Lightning Layout For Building & Shelter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0108-EL-TR-1547 |  |  | Transmital Date: 25-Oct-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised as AFC after finalizing or minor comments on "Calculation Note For Earthing & Lightning System" and latest revision of relevant Architectural Drawing document for building and shelters. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | لحاظ خواهد شد.
2 | Earthing system in switchgear building for new MV&LV switchgears, MV&LV Capacitor banks panel, MCC, Lighting and DC charger panels, battery rack, RCP, IRP, Fuse box, etc shall be shown in document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | با توجه به اینکه در مدرک Overall Earthing Layout نحوه اریتنگ تجهیزات و تابلوهای داخل سوییچگیر نشان داده شده است، لذا از اعمال آن در این مدرک صرف نظر شده است. برای اطلاعات تکمیلی به ترنسمیتال 1767 مراجعه گردد.
3 | Earthing system in CCTV&control buildings for Lighting panel, DC charger and AC UPS panels, battery rack, Fuse box, etc shall be shown in document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید.
4 | Lightning system for Fire water pump shelter and CCTV control room shall be shown. (If required base on Lightning Protection Risk Calculation in next revision) |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | با توجه به اینکه در محاسبات نیاز به درنظر گرفتن سیستم صاعقه گیر برای شلتر آب آتش نشانی می باشد، لذا صفحه 8ام اضافه گردید.
5 | Zone of Protection depicting rolling sphere method shall be shown base on NFPA 780 to check zone protection is enough or not. Meanwhile the distance between air rods shall be rechecked base on above mentioned standard. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | با توجه اینکه محاسبات صاعقه گیر بر اساس استاندارد BS صورت گرفته، فاصله مذکور رعایت شده و تعداد Air Rod بر آن اساس جانمایی شده است.
6 | Base on scope of work and supply, earthing system for CCTV control room (Less than 2 Ohm) will be calculated and shown in which document? |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | ارتینگ ساختمان CCTV به سیستم ارت موجود که زیر یک اهم می باشد، متصل می گردد و نیاز به محاسبه مجدد آن نیست.
7 | It shall be clarify the number of rods around control building and utility shelter has been been shown base on which calculation? (There is conflict between this document and Calculation Note For Earthing & Lightning System) |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | پیکربندی سیستم ارت در ویرایش جدید مدرک محاسباتی اعمال خواهد شد.
8 | "L" type earthing system around control building has been shown base on which calculation? It is recommended to show in overall earthing layout. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08
9 | It is recommended to install earth bar under false floor in control building wherever possible. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | این موارد در زمان اجرا با توجه به نوع اجرا توسط پیمانکار در بهترین موقعیت در نظر گرفته خواهد شد.
10 | Following notes shall be added: -All non-carrying current metallic part such as stairs, ladders, doors, windows, crain and etc shall be connected to earth system according to "BK-GNRAL-PEDCO-000-EL-DW-0002 Typical Installation Details & Notes For Earthing and Lightning Protection System". |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید.
11 | Typical installation detail No. shall be added on layout base on Typical Installation Details & Notes For Earthing and Lightning Protection System. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | اعمال گردید.
12 | See attach file for civil comments. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | این کامنت در بخش معماری لحاظ خواهد شد.
13 | Complementary comments will be submitted after receiving revised document. |  | BK-SUR-ENG-ELE-01-06133 | 2022-11-08 | در صورت وجود تغییرات این مدرک مورد ویرایش قرار خواهد گرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Nov-22 |  |  |  |  | Date: