## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-HV-CN-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date: 26/11/2022
Document Title: HVAC Calculation Note For Switchgear Building-W007s |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1441 |  |  | Transmital Date: 26/11/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0002-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در محاسبات تهویه اتاق باتری لحاظ نگردیده است. دمای اتاق نذکور باید 24درجه سانتیگراد باشد. |  | 01/2294/325652 | 1401/09/02 | براساس مبانی طراحی پروژه، کنترل دمای اتاق باتری نیاز نمیباشد.
2 | در جدول صفحه 18، ارتفاع و مساحت اتاق باتری گنجانده شود. |  | 01/2294/325652 | 1401/09/02 | انجام شد.
3 | میزان heat dissipation برای فضای Switchgear برچه اساس انتخاب شده است. مستندات ارائه شود. |  | 01/2294/325652 | 1401/09/02 | براساس اطلاعات موجود در پروژه های مشابه و با اعمال ضریب مناسب محاسبه شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H. Adineh | Signature
| Date: |  |  |  |  | Date: 19/02/2023