## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-HV-CN-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1441 |  |  | Transmital Date: 26/11/2022
Document Title: HVAC Calculation Note For Switchgear Building - W007S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1441 |  |  | Transmital Date: 26/11/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-HV-CN-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | to explain reason why for roof and external walls insulation has not considered.The value of U is not correct for external wall and roof, because the coefficient of thermal conductivity for rock wool with a density of 40 ~ 100 kg/m3 is 0.042 w/m2 so for rock wool insulation with 50 mm thickness R will be 1.19 m2.K/W (not 1 or 2.4 as it is mentioned in page 8 of 19). |  | BK-SUR-ENG-HVC-01-05780 | 2022-10-02 | Done.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 10/01/2022 |  |  |  |  | Date:20/02/2023