## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 19
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0001 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT INDEX نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | FEB.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | SEP.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | APR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708967
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 19
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0001 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 | X | X | X | [5 empty] | 74
11 | X | X | X | [5 empty] | 75
12 | X | X | X | [5 empty] | 76
13 | X | X | X | [5 empty] | 77
14 | X | X | X | [5 empty] | 78
15 | X | X | X | [5 empty] | 79
16 | X | X | X | [5 empty] | 80
17 | X | X | X | [5 empty] | 81
18 | X | X | X | [5 empty] | 82
19 |  | X | X | [5 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0001 | D02
REFERENCES:
| Symbol & Legend For PFD and P&ID | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D03
| Specification For Instrumentation | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001_D04
| Control/ESD/F&G System Block Diagram Configuration | [8 empty] | BK-GCS-PEDCO-120-IN-BD-0001_D05
| P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D05
| P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D05
| P&ID - Slug Catcher System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D05
| P&ID - Gas Compression Inlet Knock Out Drum | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D05
| P&ID - 1st Stage Gas Compression Suction Drums | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D05
| P&ID - 1st Stage Gas Compression Compressors | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D05
| P&ID - 1st Stage Gas Compression Air Coolers | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D05
| P&ID - 2nd Stage Gas Compression Suction Drums | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D05
| P&ID - 2nd Stage Gas Compression Compressors | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D05
| P&ID - 2nd Stage Gas Compression Air Coolers | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D05
| P&ID - 2nd Stage Gas Compression Discharge Drum | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D05
| P&ID - Gas Compression Dehydration Package | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D05
| P&ID - Lean Glycol Storage Tank | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D05
| P&ID - Instrument & Plant Air System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D05
| P&ID - Nitrogen Generation System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D05
| P&ID - Close Drain System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D05
| P&ID - Corrosion Inhibitor Package | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D05
| P&ID - Methanol Injection Package | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D05
| P&ID - LP Flare System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D05
| P&ID - Oily Water Sewer | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D05
| P&ID - Fuel Gas System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D05
| P&ID - Diesel Oil System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D05
| P&ID - Potable Water System | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D05
| P&ID - Glycol Sump Drum | [8 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D05
| P&ID - Fire Water Network | [8 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D01
| P&ID - Total Flooding System For Extension of Existing Elect. Building | [8 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
| P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [8 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D04
ABBREVIATIONS:
|  | CC | CORROSION COUPON
|  | CP/T | CORROSION PROBE/ TRANSMITTER
|  | LSLL | LEVEL SWITCH LOW LOW LEVEL SHUTDOWN
|  | LG/LIT | LEVEL GAUGE/LEVEL INDICATOR TRANSMITTER
|  | PRV/PSV | PRESSURE RILIEF VALVE/SAFTEY VALVE
|  | TRV | TEMPERATURE RILIEF VALVE
|  | PG/PT/PIT | PRESSURE GAUGE/PRESSURE TRANSMITTER/PRESSURE INDICATOR TRANSMITTER
|  | TG/TIT | TEMPERATURE GAUGE/TEMPERATURE INDICATOR TRANSMITTER
|  | ESDV | EMERGENCY SHUTDOWN VALVE
|  | XV | ON/OFF VALVE
|  | BDV | BLOWDOWN VALVE
|  | FE | FLOW ELEMENT
|  | FT | FLOW TRANSMITTER
|  | FCV/LCV/TCV | FLOW CONTROL VALVE/LEVEL CONTROL VALVE/TEMPERATURE CONTROL VALVE
|  | IS | INTRINSICALLY SAFE
|  | R | REDUNDANT
|  | AO/AI | ANALOG OUTPUT/ANALOG INPUT
|  | DO/DI | DIGITAL OUTPUT/DIGITAL INPUT
NOTE.1 : DESIGN PRESSURE BY VENDOR
NOTE.2 : ALL OF TEMPERATURE GAUGES & TEMPERATURE TRANSMITTERS SHALL BE SUPPLIED WITH THERMOWELL.
D02

## Instrument Index
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0001 |  | D00
IDENTIFICATION |  |  |  | REFERENCE | [7 empty] | PRESSURE |  | TEMPERATURE |  | INSTRUMENT RANGE | CALIBRATION RANGE | INSTRUMENT UNIT | CONTROL SYSTEM (FROM/TO) | I/O TYPE | SIGNAL TYPE | NOTE | REV.
ITEM | PROJECT PART | TAG NAME | DESCRIPTION | LINE/ EQUIPMENT | P&ID NO. | SERVICE | LOCATION/ PACKAGE NAME | DATA SHEET NO. | HOOK UP DWG. NO. | LOOP DWG NO. | LOCAION LAYOUT DWG NO. | DESIGN (BARG) | OPER. (BARG) | DESIGN (°C) | OPER. (°C)
Instrument Index for GCS
1 | General |  | Hand held calibrator | - | -
2 | General |  | Corrosion Portable Meter | - | -
3 | Gas Compression Inlet Gas Pipeline (Binak) | PG-2101 | Pressure Gauge (Bourdon) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
4 | Gas Compression Inlet Gas Pipeline (Binak) | EZSC-2101 | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
5 | Gas Compression Inlet Gas Pipeline (Binak) | EZSO-2101 | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
6 | Gas Compression Inlet Gas Pipeline (Binak) | ESOV-2101 | ESD Solenoid Valve | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER
7 | Gas Compression Inlet Gas Pipeline (Binak) | ESDV-2101 | Emergency Shut Down Valve | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67
8 | Gas Compression Inlet Gas Pipeline (Binak) | PG-2102 | Pressure Gauge (Bourdon) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
9 | Gas Compression Inlet Gas Pipeline (Binak) | PIT-2102 | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | VTA | 0-15 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
10 | Gas Compression Inlet Gas Pipeline (Binak) | TIT-2102 | Temperature Indicating Transmitter (RTD) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
11 | Gas Compression Inlet Gas Pipeline (Binak) | FE-2101 | Flow Element (Orifice Plate) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | - | - | - | -
12 | Gas Compression Inlet Gas Pipeline (Binak) | FIT-2101 | Flow Indicating Transmitter (Diaphragm) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0012 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - |  | FIELD-DCS | AI-IS-R | 4-20 mA
13 | Gas Compression Inlet Gas Pipeline (Binak) | FCV-2101 | Flow Control Valve (Globe Valve) | GAS-111-0001-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
14 | Gas Compression Inlet Gas Pipeline (Binak) | FG-2101 | Rotameter | CHM-112-0001-AS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0002 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 13.9 | 7.7 | 85 | AMB | - | - |  | - | - | -
15 | Gas Compression Inlet Gas Pipeline (Binak) | CP-2101 | Corrosion Probe (LPR probes) | GAS-111-0101-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | mm | - | - | - |  | D02 Modified
16 | Gas Compression Inlet Gas Pipeline (Binak) | CC-2101 | Corrosion Coupon (Strip Ladder) | GAS-111-0101-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0002 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 18.2 | 7.5 | 85 | 46.11/26.67 | - | - | mm | - | - | - |  | D02 Modified
17 | Gas Compression Inlet Gas Pipeline (Golkhari) | PG-2103 | Pressure Gauge (Bourdon) | GAS-111-0010-FN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
18 | Gas Compression Inlet Gas Pipeline (Golkhari) | EZSC-2102 | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0010-FN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC |  | D02 Modified
19 | Gas Compression Inlet Gas Pipeline (Golkhari) | EZSO-2102 | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0010-FN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC |  | D02 Modified
20 | Gas Compression Inlet Gas Pipeline (Golkhari) | ESOV-2102 | ESD Solenoid Valve | GAS-111-0010-FN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER |  | D02 Modified
21 | Gas Compression Inlet Gas Pipeline (Binak) | ESDV-2102 | Emergency Shut Down Valve (Ball Valve) | GAS-111-0010-FN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | [7 empty] | D02 Modified
22 | Gas Compression Inlet Gas Pipeline (Golkhari) | PG-2104 | Pressure Gauge (Bourdon) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
23 | Gas Compression Inlet Gas Pipeline (Golkhari) | PIT-2104 | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | VTA | 0-15 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
24 | Gas Compression Inlet Gas Pipeline (Golkhari) | TIT-2104 | Temperature Indicating Transmitter (RTD) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
25 | Gas Compression Inlet Gas Pipeline (Golkhari) | FE-2102 | Flow Element (Orifice Plate) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | - | - | - | - |  | D02 Modified
26 | Gas Compression Inlet Gas Pipeline (Golkhari) | FIT-2102 | Flow Indicating Transmitter (Diaphragm) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0012 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - |  | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
27 | Gas Compression Inlet Gas Pipeline (Golkhari) | FCV-2102 | Flow Control Valve (Globe Valve) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA |  | D02 Modified
28 | Gas Compression Inlet Gas Pipeline (Golkhari) | FG-2102 | Rotameter | CHM-112-0002-AS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0003 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 13.9 | 7.7 | 85 | AMB | - | - | - | - | - | -
29 | Gas Compression Inlet Gas Pipeline (Golkhari) | CP-2102 | Corrosion Probe (LPR probes) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | mm | - | - | - |  | D02 Modified
30 | Gas Compression Inlet Gas Pipeline (Golkhari) | CC-2102 | Corrosion Coupon (Strip Ladder) | GAS-111-0001-FN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0003 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 41.2 | 7.5 | 85 | 32/15.5 | - | - | mm | - | - | - |  | D02 Modified
32 | Slug Catcher System | PIT-2111 | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0012-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | VTA | 0-11 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
33 | Slug Catcher System | PSV-2111 | Pressure Safety Valve | GAS-111-0013-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | - | - | - | - | - | -
34 | Slug Catcher System | PSV-2112 | Pressure Safety Valve | GAS-111-0014-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | - | - | Barg | - | - | -
35 | Slug Catcher System | LIT-2112 | Level Indicating Transmitter (DP) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 3) | HC+WATER | V-2104 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
36 | Slug Catcher System | PIT-2112 | Pressure Indicating Transmitter (Diaphragm) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | HC+WATER | V-2104 | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | VTA | 0-11 barg | Barg | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
37 | Slug Catcher System | TG-2111 | Temperature Gauge (Bimetal) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | HC+WATER | V-2104 | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | 0-100 °C | - | °C | - | - | - | Note 2 | D02 Modified
38 | Slug Catcher System | PG-2111 | Pressure Gauge (Bourdon) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | HC+WATER | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 32/15.5 | 0-10 barg | - | Barg | - | - | - |  | D02 Modified
39 | Slug Catcher System | PDIT-2111 | Differential Pressure Indicating Transmitter (Diaphragm) | GAS-111-0019-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | HC+WATER | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
40 | Slug Catcher System | CP-2111 | Corrosion Probe (LPR probes) | GAS-111-0019-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | - | - | mm | - | - | - |  | D02 Modified
41 | Slug Catcher System | CC-2111 | Corrosion Coupon (Strip Ladder) | GAS-111-0019-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | - | - | mm | - | - | - | - | D02 Modified
42 | Slug Catcher System | LG-2111A | Level Gauge (Reflex) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | LIQUID | V-2104 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | VTA |  | - | - | - | - |  | D02 Modified
43 | Slug Catcher System | LG-2111B | Level Gauge (Reflex) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | LIQUID | V-2104 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | [7 empty] | D02 Modified
44 | Slug Catcher System | LIT-2111 | Level Indicating Transmitter (DP) | V-2104 | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) | LIQUID | V-2104 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 31.86/15.35 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA
61 | Slug Catcher System | PG-2114A | Pressure Gauge (Bourdon) | CDH-111-0010-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | 0-60 barg | - | Barg | - | - | -
62 | Slug Catcher System | PIT-2114A | Pressure Indicating Transmitter (Diaphragm) | CDH-111-0010-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | VTA | 0-11 barg | Barg | FIELD-ESD | AI-IS-R
63 | Slug Catcher System | PDG-2114A | Differential Pressure Gauge (Diaphragm) | CDH-111-0010-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | VTA | 0-1 bara | Bara | - | - | -
64 | Slug Catcher System | TG-2112A | Temperature Gauge (Bimetal) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | 0-100 °C | - | °C | - | - | - | Note 2 | D02 Modified
65 | Slug Catcher System | PG-2113A | Pressure Gauge (Bourdon) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | 0-60 barg | - | Barg | - | - | - |  | D02 Modified
66 | Slug Catcher System | PIT-2116A | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 |  | 0-39 barg |  | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
67 | Slug Catcher System | FE-2111 | Flow Element (Orifice Plate) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | - | - | - | - | - | - | - | D02 Modified
68 | Slug Catcher System | FIT-2111 | Flow Indicating Transmitter (Diaphragm) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0012 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | - | - | - | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
69 | Slug Catcher System | FCV-2111 | Flow Control Valve (Globe Valve) | CDH-112-0012-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA |  | D02 Modified
70 | Slug Catcher System | PIT-2114 | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | VTA | 0-36 barg | Barg | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
71 | Slug Catcher System | EZSC-2112 | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | - | - | - | FIELD-ESD | DI-NIS-R | 24 VDC |  | D02 Modified
72 | Slug Catcher System | EZSO-2112 | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | - | - | - | FIELD-ESD | DI-NIS-R | 24 VDC |  | D02 Modified
73 | Slug Catcher System | ESOV-2112 | ESD Solenoid Valve | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER |  | D02 Modified
74 | Slug Catcher System | XV-2112 | ON/OFF VAVLE (Ball Valve) | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | - | - | - |  |  |  |  | D02 Modified
75 | Slug Catcher System | PIT-2115 | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0015-CN07-4"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 16.5 | 85 | 24.22 | VTA | 0-36 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
76 | Slug Catcher System | TG-2112B | Temperature Gauge (Bimetal) | CDH-112-0013-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 23.3 | 19.5 | 85 | 23.22/8.82 | 0-100 °C | - | °C | - | - | - | Note 2 | D02 Modified
77 | Slug Catcher System | PG-2113B | Pressure Gauge (Bourdon) | CDH-112-0013-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 4.67 | 1.26 | 85 | 23.22/8.82 | 0-2 barg | - | Barg | - | - | -
78 | Slug Catcher System | PIT-2116B | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0013-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 24.1 | 19.5 | 85 | AMB | VTA | 0-39 barg | Barg | FIELD-DCS | AI-IS-NR | 4-20 mA
79 | Slug Catcher System | PG-2114B | Pressure Gauge (Bourdon) | CDH-111-0011-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | 0-2 barg | - | Barg | - | - | -
80 | Slug Catcher System | PIT-2114B | Pressure Indicating Transmitter (Diaphragm) | CDH-111-0011-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | VTA | 0-11 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
81 | Slug Catcher System | PDG-2114B | Differential Pressure Gauge (Diaphragm) | CDH-111-0011-AS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.5 | 85 | 23.22/8.82 | VTA | 0-1 bara | Bara | - | - | -
82 | Gas Compression Inlet Knock Out Drum | FG-2111 | Rotameter | CHM-112-0003-AS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | VTA | - | - | - | - | -
83 | Gas Compression Inlet Knock Out Drum | TIT-2112 | Temperature Indicating Transmitter (RTD) | GAS-111-0005-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
84 | Gas Compression Inlet Knock Out Drum | PIT-2116 | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0005-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | 0-11 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
85 | Gas Compression Inlet Knock Out Drum | LIT-2117 | Level Indicating Transmitter (DISPLACER) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | V-2105 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA
86 | Gas Compression Inlet Knock Out Drum | PIT-2117 | Pressure Indicating Transmitter (Diaphragm) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | V-2105 | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | 0-11 barg | Barg | FIELD-DCS | AI-IS-NR | 4-20 mA
87 | Gas Compression Inlet Knock Out Drum | TG-2113 | Temperature Gauge (Bimetal) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | V-2105 | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | 0-100 °C | - | °C | - | - | - | Note 2
88 | Gas Compression Inlet Knock Out Drum | PG-2114 | Pressure Gauge (Bourdon) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | V-2105 | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | 0-10 barg | - | Barg | - | - | -
89 | Gas Compression Inlet Knock Out Drum | PDIT-2112 | Differential Pressure Indicating Transmitter (Diaphragm) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | V-2105 | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA
92 | Gas Compression Inlet Knock Out Drum | LG-2116 | Level Gauge (Reflex) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | V-2105 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | - | - | - | - | -
93 | Gas Compression Inlet Knock Out Drum | LIT-2119 | Level Indicating Transmitter (DP) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | V-2105 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA
94 | Gas Compression Inlet Knock Out Drum | LCV-2114 | Level Control Valve (Globe Valve) | CDH-111-0019-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
95 | Gas Compression Inlet Knock Out Drum | LIT-2118 | Level Indicating Transmitter (DISPLACER) | V-2105 | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | V-2105 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA
96 | Gas Compression Inlet Knock Out Drum | EZSC-2113 | Limit Switch Close (Included in ON-OFF Valve) | CDH-111-0019-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
97 | Gas Compression Inlet Knock Out Drum | EZSO-2113 | Limit Switch Open (Included in ON-OFF Valve) | CDH-111-0019-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
98 | Gas Compression Inlet Knock Out Drum | ESOV-2113 | ESD Solenoid Valve | CDH-111-0019-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER
99 | Gas Compression Inlet Knock Out Drum | ESDV-2113 | Emergency Shut Down Valve (Ball Valve) | CDH-111-0019-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | -
100 | Gas Compression Inlet Knock Out Drum | PSV-2113 | Pressure Safety Valve | GAS-111-0021-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | -
101 | Gas Compression Inlet Knock Out Drum | PSV-2114 | Pressure Safety Valve | GAS-111-0022-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | Barg | - | - | - | -
102 | Gas Compression Inlet Knock Out Drum | CP-2112 | Corrosion Probe (LPR probes) | GAS-111-0025-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | mm | - | - | - | -
103 | Gas Compression Inlet Knock Out Drum | CC-2112 | Corrosion Coupon (Strip Ladder) | GAS-111-0025-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | mm | - | - | - | -
104 | Gas Compression Inlet Knock Out Drum | TG-2114 | Temperature Gauge (Bimetal) | GAS-111-0025-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | 0-100 °C | - | °C | - | - | - | Note 2
105 | Gas Compression Inlet Knock Out Drum | PG-2115 | Pressure Gauge (Bourdon) | GAS-111-0025-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | 0-10 barg | - | Barg | - | - | -
106 | Gas Compression Inlet Knock Out Drum | XZSC-2110 | Limit Switch Close (Included in ON-OFF Valve) | FL-112-0017-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | By Vendor
107 | Gas Compression Inlet Knock Out Drum | XZSO-2110 | Limit Switch Open (Included in ON-OFF Valve) | FL-112-0017-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | By Vendor
108 | Gas Compression Inlet Knock Out Drum | XV-2110 | ON/OFF VAVLE (Ball Valve) | FL-112-0017-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | - | -
109 | Gas Compression Inlet Knock Out Drum | PSOV-2110 | Process Solenoid Valve | FL-112-0017-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | -
110 | Gas Compression Inlet Knock Out Drum | RO-2112 | Restriction Orifice | FL-112-0017-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0005 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | -
111 | 1st Stage Gas Compression Suction Drums | PIT-2121A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031A-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
112 | 1st Stage Gas Compression Suction Drums | PCV-2123A (By Compressor Vendor) | Pressure Control Valve (Globe Valve) | GAS-111-0045A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | UCP | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
113 | 1st Stage Gas Compression Suction Drums | CZSC-2123A (By Compressor Vendor) | Limit Switch Close (Included in Control Valve) | GAS-111-0045A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
114 | 1st Stage Gas Compression Suction Drums | CZSO-2123A (By Compressor Vendor) | Limit Switch Open (Included in Control Valve) | GAS-111-0045A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
115 | 1st Stage Gas Compression Suction Drums | PSV-2121A | Pressure Safety Valve | GAS-111-0029A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | -
116 | 1st Stage Gas Compression Suction Drums | LIT-2122A | Level Indicating Transmitter | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | V-2101-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA
117 | 1st Stage Gas Compression Suction Drums | TG-2121A | Temperature Gauge (Bimetal) | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | V-2101-A | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-100 °C | - | °C | - | - | - | Note 2
118 | 1st Stage Gas Compression Suction Drums | PG-2121A | Pressure Gauge (Bourdon) | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-10 barg | - | Barg | - | - | -
119 | 1st Stage Gas Compression Suction Drums | PDIT-2121A | Differential Pressure Indicating Transmitter (Diaphragm) | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | V-2101-A | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA
120 | 1st Stage Gas Compression Suction Drums | LG-2121A | Level Gauge (Reflex) | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | V-2101-A | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | - | - | -
121 | 1st Stage Gas Compression Suction Drums | LIT-2121A | Level Indicating Transmitter (DISPLACER) | V-2101-A | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | V-2101-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
122 | 1st Stage Gas Compression Suction Drums | XZSC-2122A | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0021A-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
123 | 1st Stage Gas Compression Suction Drums | XZSO-2122A | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0021A-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
124 | 1st Stage Gas Compression Suction Drums | XV-2122A | ON/OFF VAVLE (Ball Valve) | CDH-112-0021A-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | - | -
125 | 1st Stage Gas Compression Suction Drums | PSOV-2122A | Process Solenoid Valve | CDH-112-0021A-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER
126 | 1st Stage Gas Compression Suction Drums | ESOV-2122A | ESD Solenoid Valve | CDH-112-0021A-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER
127 | 1st Stage Gas Compression Suction Drums | XZSC-2121A | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0026A-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - |  |  | -
128 | 1st Stage Gas Compression Suction Drums | XZSO-2121A | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0026A-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - |  |  | -
129 | 1st Stage Gas Compression Suction Drums | PSOV-2121A | Process Solenoid Valve | GAS-111-0026A-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | UCP-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
130 | 1st Stage Gas Compression Suction Drums | ESOV-2121A | ESD Solenoid Valve | GAS-111-0026A-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
131 | 1st Stage Gas Compression Suction Drums | XV-2121A | ON/OFF VAVLE (Ball Valve) | GAS-111-0026A-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | - | -
132 | 1st Stage Gas Compression Suction Drums | PIT-2121B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031B-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
133 | 1st Stage Gas Compression Suction Drums | PCV-2123B | Pressure Control Valve (Globe Valve) | GAS-111-0045B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | UCP | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
134 | 1st Stage Gas Compression Suction Drums | CZSC-2123B (By Compressor Vendor) | Limit Switch Close (Included in Control Valve) | GAS-111-0045A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
135 | 1st Stage Gas Compression Suction Drums | CZSO-2123B (By Compressor Vendor) | Limit Switch Open (Included in Control Valve) | GAS-111-0045A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
136 | 1st Stage Gas Compression Suction Drums | PSV-2121B | Pressure Safety Valve | GAS-111-0029B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | -
137 | 1st Stage Gas Compression Suction Drums | LIT-2122B | Level Indicating Transmitter (DISPLACER) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | V-2101-B | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
138 | 1st Stage Gas Compression Suction Drums | TG-2121B | Temperature Gauge (Bimetal) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | V-2101-B | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-100 °C | - | °C | - | - | - | Note 2
139 | 1st Stage Gas Compression Suction Drums | PG-2121B | Pressure Gauge (Bourdon) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-10 barg | - | Barg | - | - | -
140 | 1st Stage Gas Compression Suction Drums | PDIT-2121B | Differential Pressure Indicating Transmitter (Diaphragm) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | V-2101-B | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA
141 | 1st Stage Gas Compression Suction Drums | LG-2121B | Level Gauge (Reflex) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | V-2101-B | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | - | - | -
142 | 1st Stage Gas Compression Suction Drums | LIT-2121B | Level Indicating Transmitter (DISPLACER) | V-2101-B | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | V-2101-B | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
143 | 1st Stage Gas Compression Suction Drums | XZSC-2122B | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0021B-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
144 | 1st Stage Gas Compression Suction Drums | XZSO-2122B | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0021B-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
145 | 1st Stage Gas Compression Suction Drums | XV-2122B | ON/OFF VAVLE (Ball Valve) | CDH-112-0021B-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | - | -
146 | 1st Stage Gas Compression Suction Drums | PSOV-2122B | Process Solenoid Valve | CDH-112-0021B-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER
147 | 1st Stage Gas Compression Suction Drums | ESOV-2122B | ESD Solenoid Valve | CDH-112-0021B-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER
148 | 1st Stage Gas Compression Suction Drums | XZSC-2121B | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0026B-AN27-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | - | -
149 | 1st Stage Gas Compression Suction Drums | XZSO-2121B | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0026B-AN27-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | - | -
150 | 1st Stage Gas Compression Suction Drums | PSOV-2121B | Process Solenoid Valve | GAS-111-0026B-AN27-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | UCP-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
151 | 1st Stage Gas Compression Suction Drums | ESOV-2121B | ESD Solenoid Valve | GAS-111-0026B-AN27-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
152 | 1st Stage Gas Compression Suction Drums | XV-2121B | ON/OFF VAVLE (Ball Valve) | GAS-111-0026B-AN27-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.3 | 85 | 37.17/19.23 | - | - | - | - | - | - | -
153 | 1st Stage Gas Compression Suction Drums | PIT-2121C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031C-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
154 | 1st Stage Gas Compression Suction Drums | PCV-2123C | Pressure Control Valve (Globe Valve) | GAS-111-0045C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | UCP | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
155 | 1st Stage Gas Compression Suction Drums | CZSC-2123C (By Compressor Vendor) | Limit Switch Close (Included in Control Valve) | GAS-111-0045C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
156 | 1st Stage Gas Compression Suction Drums | CZSO-2123C (By Compressor Vendor) | Limit Switch Open (Included in Control Valve) | GAS-111-0045C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | By Compressor Vendor | 62 | 54.1 | 175 | 60 | - | - | - | - | - | -
157 | 1st Stage Gas Compression Suction Drums | PSV-2121C | Pressure Safety Valve | GAS-111-0029C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | -
158 | 1st Stage Gas Compression Suction Drums | LIT-2122C | Level Indicating Transmitter (DISPLACER) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | V-2101-C | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
159 | 1st Stage Gas Compression Suction Drums | TG-2121C | Temperature Gauge (Bimetal) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | V-2101-C | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-100 °C | - | °C | - | - | - | Note 2
160 | 1st Stage Gas Compression Suction Drums | PG-2121C | Pressure Gauge (Bourdon) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | 0-10 barg | - | Barg | - | - | -
161 | 1st Stage Gas Compression Suction Drums | PDIT-2121C | Differential Pressure Indicating Transmitter (Diaphragm) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | V-2101-C | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA
162 | 1st Stage Gas Compression Suction Drums | LG-2121C | Level Gauge (Reflex) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | V-2101-C | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | - | - | -
163 | 1st Stage Gas Compression Suction Drums | LIT-2121C | Level Indicating Transmitter (DISPLACER) | V-2101-C | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | V-2101-C | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.92 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
164 | 1st Stage Gas Compression Suction Drums | XZSC-2122C | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0021C-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
165 | 1st Stage Gas Compression Suction Drums | XZSO-2122C | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0021C-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
166 | 1st Stage Gas Compression Suction Drums | XV-2122C | ON/OFF VAVLE (Ball Valve) | CDH-112-0021C-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | - | - | - | -
167 | 1st Stage Gas Compression Suction Drums | PSOV-2122C | Process Solenoid Valve | CDH-112-0021C-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER
168 | 1st Stage Gas Compression Suction Drums | ESOV-2122C | ESD Solenoid Valve | CDH-112-0021C-AS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER
169 | 1st Stage Gas Compression Suction Drums | XZSC-2121C | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0026C-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.1 | 85 | 36.9/19.0 | - | - | - | - | - | - | -
170 | 1st Stage Gas Compression Suction Drums | XZSO-2121C | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0026C-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.1 | 85 | 36.9/19.0 | - | - | - | - | - | - | -
171 | 1st Stage Gas Compression Suction Drums | PSOV-2121C | Process Solenoid Valve | GAS-111-0026C-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.1 | 85 | 36.9/19.0 | - | - | - | UCP-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
172 | 1st Stage Gas Compression Suction Drums | ESOV-2121C | ESD Solenoid Valve | GAS-111-0026C-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.1 | 85 | 36.9/19.0 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
173 | 1st Stage Gas Compression Suction Drums | XV-2121C | ON/OFF VAVLE (Ball Valve) | GAS-111-0026C-AN07-8"-PT | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 5.1 | 85 | 36.9/19.0 | - | - | - | - | - | - | -
174 | 1st Stage Gas Compression Compressors | TG-2122A | Temperature Gauge (Bimetal) | GAS-111-0031A-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | - | - | - | Note 2
175 | 1st Stage Gas Compression Compressors | TIT-2121A | Temperature Indicating Transmitter (RTD) | GAS-111-0031A-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
176 | 1st Stage Gas Compression Compressors | PIT-2122A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031A-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
177 | 1st Stage Gas Compression Compressors | PG-2122A | Pressure Gauge (Bourdon) | GAS-111-0031A-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-10 barg | - | Barg | - | - | -
178 | 1st Stage Gas Compression Compressors | PSV-2122A | Pressure Safety Valve | GAS-111-0032A-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
179 | 1st Stage Gas Compression Compressors | PSV-2123A | Pressure Safety Valve | GAS-111-0033A-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
180 | 1st Stage Gas Compression Compressors | PIT-2125A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0036A-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | VTA | 0-38 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
181 | 1st Stage Gas Compression Compressors | TIT-2124A | Temperature Indicating Transmitter (RTD) | GAS-111-0036A-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
182 | 1st Stage Gas Compression Compressors | TG-2123A | Temperature Gauge (Bimetal) | GAS-111-0036A-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | - | - | - | Note 2
183 | 1st Stage Gas Compression Compressors | PG-2123A | Pressure Gauge (Bourdon) | GAS-111-0036A-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-40 barg | - | Barg | - | - | -
184 | 1st Stage Gas Compression Compressors | TG-2122B | Temperature Gauge (Bimetal) | GAS-111-0031B-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | - | - | - | Note 2
185 | 1st Stage Gas Compression Compressors | TIT-2121B | Temperature Indicating Transmitter (RTD) | GAS-111-0031B-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
186 | 1st Stage Gas Compression Compressors | PIT-2122B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031B-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
187 | 1st Stage Gas Compression Compressors | PG-2122B | Pressure Gauge (Bourdon) | GAS-111-0031B-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-10 barg | - | Barg | - | - | -
188 | 1st Stage Gas Compression Compressors | PSV-2122B | Pressure Safety Valve | GAS-111-0032B-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
189 | 1st Stage Gas Compression Compressors | PSV-2123B | Pressure Safety Valve | GAS-111-0033B-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
190 | 1st Stage Gas Compression Compressors | PIT-2125B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0036B-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | VTA | 0-38 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
191 | 1st Stage Gas Compression Compressors | TIT-2124B | Temperature Indicating Transmitter (RTD) | GAS-111-0036B-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
192 | 1st Stage Gas Compression Compressors | TG-2123B | Temperature Gauge (Bimetal) | GAS-111-0036B-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | - | - | - | Note 2
193 | 1st Stage Gas Compression Compressors | PG-2123B | Pressure Gauge (Bourdon) | GAS-111-0036B-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-40 barg | - | Barg | - | - | -
194 | 1st Stage Gas Compression Compressors | TG-2122C | Temperature Gauge (Bimetal) | GAS-111-0031C-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | - | - | - | Note 2
195 | 1st Stage Gas Compression Compressors | TIT-2121C | Temperature Indicating Transmitter (RTD) | GAS-111-0031C-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
196 | 1st Stage Gas Compression Compressors | PIT-2122C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0031C-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | VTA | 0-10 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
197 | 1st Stage Gas Compression Compressors | PG-2122C | Pressure Gauge (Bourdon) | GAS-111-0031C-AN05-8"-ET | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.78/18.88 | 0-10 barg | - | Barg | - | - | -
198 | 1st Stage Gas Compression Compressors | PSV-2122C | Pressure Safety Valve | GAS-111-0032C-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
199 | 1st Stage Gas Compression Compressors | PSV-2123C | Pressure Safety Valve | GAS-111-0033C-CN05-3"-PT | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | - | - | - | - | - | -
200 | 1st Stage Gas Compression Compressors | PIT-2125C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0036C-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | VTA | 0-38 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
201 | 1st Stage Gas Compression Compressors | TIT-2124C | Temperature Indicating Transmitter (RTD) | GAS-111-0036C-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
202 | 1st Stage Gas Compression Compressors | TG-2123C | Temperature Gauge (Bimetal) | GAS-111-0036C-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-250 °C | - | °C | - | - | - | Note 2
203 | 1st Stage Gas Compression Compressors | PG-2123C | Pressure Gauge (Bourdon) | GAS-111-0036C-CN05-6"-NP | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 19 | 155 | 124.8/113.1 | 0-40 barg | - | Barg | - | - | -
204 | 1st Stage Gas Compression Air Coolers | TIT-2126A | Temperature Indicating Transmitter (RTD) | GAS-111-0037A-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
205 | 1st Stage Gas Compression Air Coolers | TIT-2125A | Temperature Indicating Transmitter (RTD) | GAS-111-0037A-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
206 | 1st Stage Gas Compression Air Coolers | TG-2124A | Temperature Gauge (Bimetal) | GAS-111-0037A-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | - | - | - | Note 2 | D02 Modified
207 | 1st Stage Gas Compression Air Coolers | PG-2124A | Pressure Gauge (Bourdon) | GAS-111-0037A-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-40 barg | - | Barg | - | - | - |  | D02 Modified
208 | 1st Stage Gas Compression Air Coolers | TIT-2126B | Temperature Indicating Transmitter (RTD) | GAS-111-0037B-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
209 | 1st Stage Gas Compression Air Coolers | TIT-2125B | Temperature Indicating Transmitter (RTD) | GAS-111-0037B-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
210 | 1st Stage Gas Compression Air Coolers | TG-2124B | Temperature Gauge (Bimetal) | GAS-111-0037B-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | - | - | - | Note 2 | D02 Modified
211 | 1st Stage Gas Compression Air Coolers | PG-2124B | Pressure Gauge (Bourdon) | GAS-111-0037B-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-40 barg | - | Barg | - | - | - |  | D02 Modified
212 | 1st Stage Gas Compression Air Coolers | TIT-2126C | Temperature Indicating Transmitter (RTD) | GAS-111-0037C-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
213 | 1st Stage Gas Compression Air Coolers | TIT-2125C | Temperature Indicating Transmitter (RTD) | GAS-111-0037C-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2 | D02 Modified
214 | 1st Stage Gas Compression Air Coolers | TG-2124C | Temperature Gauge (Bimetal) | GAS-111-0037C-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-160 °C | - | °C | - | - | - | Note 2 | D02 Modified
215 | 1st Stage Gas Compression Air Coolers | PG-2124C | Pressure Gauge (Bourdon) | GAS-111-0037C-CS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 22 | 18.3 | 150 | 60 | 0-40 barg | - | Barg | - | - | - |  | D02 Modified
216 | 2nd Stage Gas Compression Suction Drums | PSV-2131A | Pressure Safety Valve | GAS-111-0042A-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
217 | 2nd Stage Gas Compression Suction Drums | LIT-2132A | Level Indicating Transmitter(DISPLACER) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | V-2102-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA | - | D02 Modified
218 | 2nd Stage Gas Compression Suction Drums | TG-2131A | Temperature Gauge (Bimetal) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | V-2102-A | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
219 | 2nd Stage Gas Compression Suction Drums | PG-2131A | Pressure Gauge (Bourdon) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-40 barg | - | Barg | - | - | -
220 | 2nd Stage Gas Compression Suction Drums | PDIT-2131A | Differential Pressure Indicating Transmitter (Diaphragm) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | V-2102-A | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | 0-1 bara | Bara | DCS | AI-IS-NR | 4-20 mA | -
221 | 2nd Stage Gas Compression Suction Drums | LG-2131A | Level Gauge (Reflex) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | V-2102-A | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | - | - | - | -
222 | 2nd Stage Gas Compression Suction Drums | LIT-2131A | Level Indicating Transmitter(DISPLACER) | V-2102-A | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | V-2102-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
223 | 2nd Stage Gas Compression Suction Drums | XZSC-2131A | Limit Switch Close (Included in ON-OFF Valve) | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
224 | 2nd Stage Gas Compression Suction Drums | XZSO-2131A | Limit Switch Open (Included in ON-OFF Valve) | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
225 | 2nd Stage Gas Compression Suction Drums | PSOV-2131A | Process Solenoid Valve | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
226 | 2nd Stage Gas Compression Suction Drums | ESOV-2131A | ESD Solenoid Valve | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
227 | 2nd Stage Gas Compression Suction Drums | XV-2131A | ON/OFF VAVLE (Ball Valve) | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
228 | 2nd Stage Gas Compression Suction Drums | RO-2131A | Restriction Orifice | CDH-111-0023A-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
229 | 2nd Stage Gas Compression Suction Drums | RO-2134A | Restriction Orifice | GAS-111-0160A-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
230 | 2nd Stage Gas Compression Suction Drums | BZSC-2134A | Limit Switch Close (Included in blowdown Valve) | FL-112-0119A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
231 | 2nd Stage Gas Compression Suction Drums | BZSO-2134A | Limit Switch Open (Included in blowdown Valve) | FL-112-0119A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
232 | 2nd Stage Gas Compression Suction Drums | BSOV-2134A | BDV Solenoid Valve | FL-112-0119A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
233 | 2nd Stage Gas Compression Suction Drums | PSOV-2134A | Process Solenoid Valve | FL-112-0119A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
234 | 2nd Stage Gas Compression Suction Drums | BDV-2134A | Blowdown valve | FL-112-0119A-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - |  | - | - | - | -
235 | 2nd Stage Gas Compression Suction Drums | PSV-2131B | Pressure Safety Valve | GAS-111-0042B-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | ` | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | ` | - | -
236 | 2nd Stage Gas Compression Suction Drums | LIT-2132B | Level Indicating Transmitter(DISPLACER) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | V-2102-B | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA | - | D02 Modified
237 | 2nd Stage Gas Compression Suction Drums | TG-2131B | Temperature Gauge (Bimetal) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | V-2102-B | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
238 | 2nd Stage Gas Compression Suction Drums | PG-2131B | Pressure Gauge (Bourdon) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-40 barg | - | Barg | - | - | -
239 | 2nd Stage Gas Compression Suction Drums | PDIT-2131B | Differential Pressure Indicating Transmitter (Diaphragm) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | V-2102-B | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA | -
240 | 2nd Stage Gas Compression Suction Drums | LG-2131B | Level Gauge (Reflex) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | V-2102-B | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | - | - | - | -
241 | 2nd Stage Gas Compression Suction Drums | LIT-2131B | Level Indicating Transmitter(DISPLACER) | V-2102-B | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | V-2102-B | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
242 | 2nd Stage Gas Compression Suction Drums | XZSC-2131B | Limit Switch Close (Included in ON-OFF Valve) | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
243 | 2nd Stage Gas Compression Suction Drums | XZSO-2131B | Limit Switch Open (Included in ON-OFF Valve) | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
244 | 2nd Stage Gas Compression Suction Drums | PSOV-2131B | Process Solenoid Valve | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
245 | 2nd Stage Gas Compression Suction Drums | ESOV-2131B | ESD Solenoid Valve | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
246 | 2nd Stage Gas Compression Suction Drums | XV-2131B | ON/OFF VAVLE (Ball Valve) | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
247 | 2nd Stage Gas Compression Suction Drums | RO-2131B | Restriction Orifice | CDH-111-0023B-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
248 | 2nd Stage Gas Compression Suction Drums | RO-2134B | Restriction Orifice | GAS-111-0160B-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
249 | 2nd Stage Gas Compression Suction Drums | BZSC-2131B | Limit Switch Close (Included in blowdown Valve) | FL-112-0119B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
250 | 2nd Stage Gas Compression Suction Drums | BZSO-2131B | Limit Switch Open (Included in blowdown Valve) | FL-112-0119B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
251 | 2nd Stage Gas Compression Suction Drums | BSOV-2131B | BDV Solenoid Valve | FL-112-0119B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
252 | 2nd Stage Gas Compression Suction Drums | PSOV-2131B | Process Solenoid Valve | FL-112-0119B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
253 | 2nd Stage Gas Compression Suction Drums | BDV-2131B | Blowdown valve | FL-112-0119B-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
254 | 2nd Stage Gas Compression Suction Drums | PSV-2131C | Pressure Safety Valve | GAS-111-0042C-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
255 | 2nd Stage Gas Compression Suction Drums | LIT-2132C | Level Indicating Transmitter(DISPLACER) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | V-2102-C | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA | - | D02 Modified
256 | 2nd Stage Gas Compression Suction Drums | TG-2131C | Temperature Gauge (Bimetal) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | V-2102-C | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
257 | 2nd Stage Gas Compression Suction Drums | PG-2131C | Pressure Gauge (Bourdon) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | 0-40 barg | - | Barg | - | - | -
258 | 2nd Stage Gas Compression Suction Drums | PDIT-2131C | Differential Pressure Indicating Transmitter (Diaphragm) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | V-2102-C | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-NR | 4-20 mA | -
259 | 2nd Stage Gas Compression Suction Drums | LG-2131C | Level Gauge (Reflex) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | V-2102-C | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | - | - | - | -
260 | 2nd Stage Gas Compression Suction Drums | LIT-2131C | Level Indicating Transmitter(DISPLACER) | V-2102-C | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | V-2102-C | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
261 | 2nd Stage Gas Compression Suction Drums | XZSC-2131C | Limit Switch Close (Included in ON-OFF Valve) | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
262 | 2nd Stage Gas Compression Suction Drums | XZSO-2131C | Limit Switch Open (Included in ON-OFF Valve) | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
263 | 2nd Stage Gas Compression Suction Drums | PSOV-2131C | Process Solenoid Valve | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
264 | 2nd Stage Gas Compression Suction Drums | ESOV-2131C | ESD Solenoid Valve | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
265 | 2nd Stage Gas Compression Suction Drums | XV-2131C | ON/OFF VAVLE (Ball Valve) | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
266 | 2nd Stage Gas Compression Suction Drums | RO-2131C | Restriction Orifice | CDH-111-0023C-CS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | - | - | - | - | - | - | -
267 | 2nd Stage Gas Compression Suction Drums | RO-2134C | Restriction Orifice | GAS-111-0160C-CN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
268 | 2nd Stage Gas Compression Suction Drums | BZSC-2131C | Limit Switch Close (Included in blowdown Valve) | FL-112-0119C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
269 | 2nd Stage Gas Compression Suction Drums | BZSO-2131C | Limit Switch Open (Included in blowdown Valve) | FL-112-0119C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
270 | 2nd Stage Gas Compression Suction Drums | BSOV-2131C | BDV Solenoid Valve | FL-112-0119C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
271 | 2nd Stage Gas Compression Suction Drums | PSOV-2131C | Process Solenoid Valve | FL-112-0119C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
272 | 2nd Stage Gas Compression Suction Drums | BDV-2131C | Blowdown valve | FL-112-0119C-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.3 | 115.5 | 60 | - | - | - | - | - | - | -
273 | 2nd Stage Gas Compression Compressors | TG-2132A | Temperature Gauge (Bimetal) | GAS-111-0044A-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | - | - | - | Note 2
274 | 2nd Stage Gas Compression Compressors | TIT-2131A | Temperature Indicating Transmitter (RTD) | GAS-111-0044A-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
275 | 2nd Stage Gas Compression Compressors | PIT-2131A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0044A-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | VTA | 0-37 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
276 | 2nd Stage Gas Compression Compressors | PG-2132A | Pressure Gauge (Bourdon) | GAS-111-0044A-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-40 barg | - | Barg | - | - | -
277 | 2nd Stage Gas Compression Compressors | PSV-2132A | Pressure Safety Valve | GAS-111-0047A-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
278 | 2nd Stage Gas Compression Compressors | PSV-2133A | Pressure Safety Valve | GAS-111-0048A-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
279 | 2nd Stage Gas Compression Compressors | PIT-2134A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0051A-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | VTA | 0-109 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
280 | 2nd Stage Gas Compression Compressors | TIT-2134A | Temperature Indicating Transmitter (RTD) | GAS-111-0051A-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
281 | 2nd Stage Gas Compression Compressors | TG-2133A | Temperature Gauge (Bimetal) | GAS-111-0051A-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | - | - | - | Note 2
282 | 2nd Stage Gas Compression Compressors | PG-2133A | Pressure Gauge (Bourdon) | GAS-111-0051A-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-100 barg | - | Barg | - | - | -
283 | 2nd Stage Gas Compression Compressors | TG-2132B | Temperature Gauge (Bimetal) | GAS-111-0044B-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | - | - | - | Note 2
284 | 2nd Stage Gas Compression Compressors | TIT-2131B | Temperature Indicating Transmitter (RTD) | GAS-111-0044B-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
285 | 2nd Stage Gas Compression Compressors | PIT-2131B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0044B-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | VTA | 0-37 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
286 | 2nd Stage Gas Compression Compressors | PG-2132B | Pressure Gauge (Bourdon) | GAS-111-0044B-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-40 barg | - | Barg | - | - | -
287 | 2nd Stage Gas Compression Compressors | PSV-2132B | Pressure Safety Valve | GAS-111-0047B-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
288 | 2nd Stage Gas Compression Compressors | PSV-2133B | Pressure Safety Valve | GAS-111-0048B-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
289 | 2nd Stage Gas Compression Compressors | PIT-2134B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0051B-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | VTA | 0-109 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
290 | 2nd Stage Gas Compression Compressors | TIT-2134B | Temperature Indicating Transmitter (RTD) | GAS-111-0051B-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
291 | 2nd Stage Gas Compression Compressors | TG-2133B | Temperature Gauge (Bimetal) | GAS-111-0051B-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | - | - | - | Note 2
292 | 2nd Stage Gas Compression Compressors | PG-2133B | Pressure Gauge (Bourdon) | GAS-111-0051B-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-100 barg | - | Barg | - | - | -
293 | 2nd Stage Gas Compression Compressors | TG-2132C | Temperature Gauge (Bimetal) | GAS-111-0044C-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | - | - | - | Note 2
294 | 2nd Stage Gas Compression Compressors | TIT-2131C | Temperature Indicating Transmitter (RTD) | GAS-111-0044C-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-NR | 4-20 mA | Note 2
295 | 2nd Stage Gas Compression Compressors | PIT-2131C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0044C-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | VTA | 0-37 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
296 | 2nd Stage Gas Compression Compressors | PG-2132C | Pressure Gauge (Bourdon) | GAS-111-0044C-CN05-6"-ET | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/22 | 18.1 | 115.5 | 59.88 | 0-40 barg | - | Barg | - | - | -
297 | 2nd Stage Gas Compression Compressors | PSV-2132C | Pressure Safety Valve | GAS-111-0047C-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
298 | 2nd Stage Gas Compression Compressors | PSV-2133C | Pressure Safety Valve | GAS-111-0048C-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | - | - | - | - | - | -
299 | 2nd Stage Gas Compression Compressors | PIT-2134C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0051C-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | VTA | 0-109 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
300 | 2nd Stage Gas Compression Compressors | TIT-2134C | Temperature Indicating Transmitter (RTD) | GAS-111-0051C-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
301 | 2nd Stage Gas Compression Compressors | TG-2133C | Temperature Gauge (Bimetal) | GAS-111-0051C-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-400 °C | - | °C | - | - | - | Note 2
302 | 2nd Stage Gas Compression Compressors | PG-2133C | Pressure Gauge (Bourdon) | GAS-111-0051C-FN05-6"-IS | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.8 | 175 | 149.5/142.3 | 0-100 barg | - | Barg | - | - | -
303 | 2nd Stage Gas Compression Air Coolers | TIT-2135A | Temperature Indicating Transmitter (RTD) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
304 | 2nd Stage Gas Compression Air Coolers | TIT-2136A | Temperature Indicating Transmitter (RTD) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
305 | 2nd Stage Gas Compression Air Coolers | TG-2134A | Temperature Gauge (Bimetal) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
306 | 2nd Stage Gas Compression Air Coolers | PG-2134A | Pressure Gauge (Bourdon) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-100 barg | - | Barg | - | - | -
307 | 2nd Stage Gas Compression Air Coolers | FG-2132A | Rotameter | CHM-112-0005A-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | -
308 | 2nd Stage Gas Compression Air Coolers | PIT-2135A | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0057A-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | VTA | 0-109 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA | -
309 | 2nd Stage Gas Compression Air Coolers | PCV-2135 | Pressure Control Valve (Globe Valve) | GAS-111-0057A-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA | -
310 | 2nd Stage Gas Compression Air Coolers | RO-2133A | Restriction Orifice | FL-112-0023A-AN07-2''-PT | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
311 | 2nd Stage Gas Compression Air Coolers | BZSC-2132A | Limit Switch Close (Included in blowdown Valve) | GAS-111-0054A-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
312 | 2nd Stage Gas Compression Air Coolers | BZSO-2132A | Limit Switch Open (Included in blowdown Valve) | GAS-111-0054A-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
313 | 2nd Stage Gas Compression Air Coolers | PSOV-2132A | Process Solenoid Valve | GAS-111-0054A-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
314 | 2nd Stage Gas Compression Air Coolers | BSOV-2132A | BDV Solenoid Valve | GAS-111-0054A-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
315 | 2nd Stage Gas Compression Air Coolers | BDV-2132A | Blowdown valve | GAS-111-0054B-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
316 | 2nd Stage Gas Compression Air Coolers | XZSC-2133A | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
317 | 2nd Stage Gas Compression Air Coolers | XZSO-2133A | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
318 | 2nd Stage Gas Compression Air Coolers | PSOV-2133A | Process Solenoid Valve | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
319 | 2nd Stage Gas Compression Air Coolers | ESOV-2133A | ESD Solenoid Valve | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
320 | 2nd Stage Gas Compression Air Coolers | XV-2133A | ON/OFF VAVLE (Ball Valve) | GAS-111-0058A-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
321 | 2nd Stage Gas Compression Air Coolers | TIT-2135B | Temperature Indicating Transmitter (RTD) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
322 | 2nd Stage Gas Compression Air Coolers | TIT-2136B | Temperature Indicating Transmitter (RTD) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
323 | 2nd Stage Gas Compression Air Coolers | TG-2134B | Temperature Gauge (Bimetal) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
324 | 2nd Stage Gas Compression Air Coolers | PG-2134B | Pressure Gauge (Bourdon) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-100 barg | - | Barg | - | - | -
325 | 2nd Stage Gas Compression Air Coolers | FG-2132B | Rotameter | CHM-112-0005B-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | -
326 | 2nd Stage Gas Compression Air Coolers | PIT-2135B | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0057B-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | VTA | 0-109 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA | -
327 | 2nd Stage Gas Compression Air Coolers | PCV-2134B | Pressure Control Valve (Globe Valve) | GAS-111-0057B-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA | -
328 | 2nd Stage Gas Compression Air Coolers | RO-2133B | Restriction Orifice | FL-112-0023B-AN07-2''-PT | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
329 | 2nd Stage Gas Compression Air Coolers | BZSC-2132B | Limit Switch Close (Included in blowdown Valve) | GAS-111-0054B-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
330 | 2nd Stage Gas Compression Air Coolers | BZSO-2132B | Limit Switch Open (Included in blowdown Valve) | GAS-111-0054B-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
331 | 2nd Stage Gas Compression Air Coolers | PSOV-2132B | Process Solenoid Valve | GAS-111-0054B-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
332 | 2nd Stage Gas Compression Air Coolers | BSOV-2132B | BDV Solenoid Valve | GAS-111-0054B-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
333 | 2nd Stage Gas Compression Air Coolers | BDV-2132B | Blowdown valve | GAS-111-0054A-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
334 | 2nd Stage Gas Compression Air Coolers | XZSC-2133B | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
335 | 2nd Stage Gas Compression Air Coolers | XZSO-2133B | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
336 | 2nd Stage Gas Compression Air Coolers | PSOV-2133B | Process Solenoid Valve | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
337 | 2nd Stage Gas Compression Air Coolers | ESOV-2133B | ESD Solenoid Valve | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
338 | 2nd Stage Gas Compression Air Coolers | XV-2133B | ON/OFF VAVLE (Ball Valve) | GAS-111-0058B-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
339 | 2nd Stage Gas Compression Air Coolers | TIT-2135C | Temperature Indicating Transmitter (RTD) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
340 | 2nd Stage Gas Compression Air Coolers | TIT-2136C | Temperature Indicating Transmitter (RTD) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | FIELD-ESD | AI-IS-R | 4-20 mA | Note 2
341 | 2nd Stage Gas Compression Air Coolers | TG-2134C | Temperature Gauge (Bimetal) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
342 | 2nd Stage Gas Compression Air Coolers | PG-2134C | Pressure Gauge (Bourdon) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | 0-100 barg | - | Barg | - | - | -
343 | 2nd Stage Gas Compression Air Coolers | FG-2132C | Rotameter | CHM-112-0005C-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | -
344 | 2nd Stage Gas Compression Air Coolers | PIT-2135C | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0057C-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | VTA | 0-109 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA | -
345 | 2nd Stage Gas Compression Air Coolers | PCV-2134C | Pressure Control Valve (Globe Valve) | GAS-111-0057C-FS00-4"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA | -
346 | 2nd Stage Gas Compression Air Coolers | RO-2133C | Restriction Orifice | FL-112-0023C-AN07-2''-PT | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
347 | 2nd Stage Gas Compression Air Coolers | BZSC-2132C | Limit Switch Close (Included in blowdown Valve) | GAS-111-0054C-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
348 | 2nd Stage Gas Compression Air Coolers | BZSO-2132C | Limit Switch Open (Included in blowdown Valve) | GAS-111-0054C-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | FIELD-DCS | DI-NIS-NR | 24 VDC | -
349 | 2nd Stage Gas Compression Air Coolers | PSOV-2132C | Process Solenoid Valve | GAS-111-0054C-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
350 | 2nd Stage Gas Compression Air Coolers | BSOV-2132C | BDV Solenoid Valve | GAS-111-0054C-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
351 | 2nd Stage Gas Compression Air Coolers | BDV-2132C | Blowdown valve | GAS-111-0054C-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
352 | 2nd Stage Gas Compression Air Coolers | XZSC-2133C | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
353 | 2nd Stage Gas Compression Air Coolers | XZSO-2133C | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | FIELD-DCS | DI-NIS-NR | 24 VDC | -
354 | 2nd Stage Gas Compression Air Coolers | PSOV-2133C | Process Solenoid Valve | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | -
355 | 2nd Stage Gas Compression Air Coolers | ESOV-2133C | ESD Solenoid Valve | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 |  |  |  | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
356 | 2nd Stage Gas Compression Air Coolers | XV-2133C | ON/OFF VAVLE (Ball Valve) | GAS-111-0058C-FS00-6"-NP | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 54.1 | 175 | 60 | - | - | - | - | - | - | -
357 | 2nd Stage Gas Compression Discharge Drum | FG-2142 | Rotameter | CHM-112-0006-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | -
358 | 2nd Stage Gas Compression Discharge Drum | FG-2141 | Rotameter | CHM-112-0010-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | - | D02 Modified
359 | 2nd Stage Gas Compression Discharge Drum | PSV-2141 | Pressure Safety Valve | GAS-111-0060-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
360 | 2nd Stage Gas Compression Discharge Drum | PSV-2142 | Pressure Safety Valve | GAS-111-0062-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
361 | 2nd Stage Gas Compression Discharge Drum | BZSC-2141 | Limit Switch Close (Included in blowdown Valve) | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
362 | 2nd Stage Gas Compression Discharge Drum | BZSO-2141 | Limit Switch Open (Included in blowdown Valve) | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
363 | 2nd Stage Gas Compression Discharge Drum | BSOV-2141 | BDV Solenoid Valve | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | - | D02 Modified
364 | 2nd Stage Gas Compression Discharge Drum | BDV-2141 | Blowdown valve | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
365 | 2nd Stage Gas Compression Discharge Drum | RO-2141 | Restriction Orifice | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
366 | 2nd Stage Gas Compression Discharge Drum | CP-2141 | Corrosion Probe (LPR probes) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | mm | - | - | - | - | D02 Modified
367 | 2nd Stage Gas Compression Discharge Drum | CC-2141 | Corrosion Coupon (Strip Ladder) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | mm | - | - | - | - | D02 Modified
368 | 2nd Stage Gas Compression Discharge Drum | PG-2142 | Pressure Gauge (Bourdon) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | 0-100 barg | - | Barg | - | - | - |  | D02 Modified
369 | 2nd Stage Gas Compression Discharge Drum | TG-2142 | Temperature Gauge (Bimetal) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | 0-160 °C | - | °C | - | - | - | Note 2 | D02 Modified
370 | 2nd Stage Gas Compression Discharge Drum | XZSC-2142 | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
371 | 2nd Stage Gas Compression Discharge Drum | XZSO-2142 | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
372 | 2nd Stage Gas Compression Discharge Drum | ESOV-2142 | ESD Solenoid Valve | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | - | D02 Modified
373 | 2nd Stage Gas Compression Discharge Drum | PSOV-2142 | Process Solenoid Valve | GAS-111-0066-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | - | D02 Modified
374 | 2nd Stage Gas Compression Discharge Drum | XV-2142 | ON/OFF VAVLE (Ball Valve) | GAS-111-0065-FN05-2"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
375 | 2nd Stage Gas Compression Discharge Drum | XZSC-2143 | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
376 | 2nd Stage Gas Compression Discharge Drum | XZSO-2143 | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | - | D02 Modified
377 | 2nd Stage Gas Compression Discharge Drum | ESOV-2143 | ESD Solenoid Valve | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | - | D02 Modified
378 | 2nd Stage Gas Compression Discharge Drum | PSOV-2143 | Process Solenoid Valve | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | - | D02 Modified
379 | 2nd Stage Gas Compression Discharge Drum | XV-2143 | ON/OFF VAVLE (Ball Valve) | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
380 | 2nd Stage Gas Compression Discharge Drum | PDIT-2143 | Differential Pressure Indicating Transmitter (Diaphragm) | GAS-111-0366-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | VTA | 0-1 bara | Bara | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
381 | 2nd Stage Gas Compression Discharge Drum | LIT-2142 | Level Indicating Transmitter (DISPLACER) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | V-2103 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA | - | D02 Modified
382 | 2nd Stage Gas Compression Discharge Drum | TG-2141 | Temperature Gauge (Bimetal) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | V-2103 | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | 0-160 °C | - | °C | - | - | - | Note 2 | D02 Modified
383 | 2nd Stage Gas Compression Discharge Drum | PG-2141 | Pressure Gauge (Bourdon) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | 0-100 barg | - | Barg | - | - | - |  | D02 Modified
384 | 2nd Stage Gas Compression Discharge Drum | PDIT-2141 | Differential Pressure Indicating Transmitter (Diaphragm) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | GAS | V-2103 | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | VTA | 0-1 bara | Barg | FIELD-DCS | AI-IS-NR | 4-20 mA | - | D02 Modified
385 | 2nd Stage Gas Compression Discharge Drum | LG-2141 | Level Gauge (Reflex) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | V-2103 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | VTA | - | - | - | - | - | - | D02 Modified
386 | 2nd Stage Gas Compression Discharge Drum | LIT-2141 | Level Indicating Transmitter (DISPLACER) | V-2103 | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | V-2103 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA | - | D02 Modified
388 | 2nd Stage Gas Compression Discharge Drum | RO-2144 | Restriction Orifice | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
389 | 2nd Stage Gas Compression Discharge Drum | XZSC-2144 | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-R | 24 VDC | - | D02 Modified
390 | 2nd Stage Gas Compression Discharge Drum | XZSO-2144 | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | FIELD-DCS | DI-NIS-R | 24 VDC | - | D02 Modified
391 | 2nd Stage Gas Compression Discharge Drum | ESOV-2144 | ESD Solenoid Valve | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | - | D02 Modified
392 | 2nd Stage Gas Compression Discharge Drum | PSOV-2144 | Process Solenoid Valve | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | DCS-FIELD | DO-NIS-NR | 24VDC LOOP POWER | - | D02 Modified
393 | 2nd Stage Gas Compression Discharge Drum | XV-2144 | ON/OFF VAVLE (Ball Valve) | CDH-112-0025-FS00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0012 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/62 | 53.9 | 130 | 59.89 | - | - | - | - | - | - | - | D02 Modified
394 | Gas Compression Dehydration Package | FG-2151 | Rotameter | CHM-112-0011-FS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | ATM | 55 | AMB | - | - | - | - | - | - | -
395 | Gas Compression Dehydration Package | BZSC-2151 | Limit Switch Close (Included in blowdown Valve) | FL-112-0002-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
396 | Gas Compression Dehydration Package | BZSO-2151 | Limit Switch Open (Included in blowdown Valve) | FL-112-0002-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
397 | Gas Compression Dehydration Package | BSOV-2151 | BDV Solenoid Valve | FL-112-0002-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
398 | Gas Compression Dehydration Package | BDV-2151 | Blowdown valve | FL-112-0002-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | - | - | -
399 | Gas Compression Dehydration Package | RO-2151 | Restriction Orifice | FL-112-0002-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | - | - | -
400 | Gas Compression Dehydration Package | PIT-2151 | Pressure Indicating Transmitter (Diaphragm) | GAS-111-0072-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | VTA | 0-105 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
401 | Gas Compression Dehydration Package | PCV-2151 | Pressure Control Valve (Globe Valve) | FL-112-0029-AN07-6"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
402 | Gas Compression Dehydration Package | PCV-2152 | Pressure Control Valve (Globe Valve) | GAS-111-0072-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
403 | Gas Compression Dehydration Package | CP-2151 | Corrosion Probe (LPR probes) | GAS-111-0072-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | mm | - | - | - | - | D02 Modified
404 | Gas Compression Dehydration Package | CC-2151 | Corrosion Coupon (Strip Ladder) | GAS-111-0072-FN05-6"-PT | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 62 | 52.9 | 85 | 59.40/59.36 | - | - | mm | - | - | - | - | D02 Modified
405 | Lean Glycol Storage Tank | TG-2161 | Temperature Gauge (Bimetal) | TEG-111-0001-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | 0-100 °C | - | °C | - | - | - | Note 2 | D02 Modified
406 | Lean Glycol Storage Tank | PG-2161 | Pressure Gauge (Diaphragm) | NIT-112-0010-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | 0-1 barg | - | Barg | - | - | - |  | D02 Modified
407 | Lean Glycol Storage Tank | PVSV-2161 | Pressure Vacation Safety Valve | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | GAS | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA | - | - | - | - | - | 1
408 | Lean Glycol Storage Tank | PVSV-2162 | Pressure Vacation Safety Valve | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | GAS | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA | - | - | - | - | -
409 | Lean Glycol Storage Tank | PRV-2161 | Pressure Relief Valve | NIT-112-0010-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.5 | 85 | AMB | VTA | - | - | - | - | -
410 | Lean Glycol Storage Tank | PRV-2162 | Pressure Relief Valve | NIT-112-0010-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA | - | - | - | - | -
412 | Lean Glycol Storage Tank | PG-2162 | Pressure Gauge (Diaphragm) | TEG-111-0007-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | 0-2.5 barg | - | Barg | - | - | -
413 | Lean Glycol Storage Tank | LG-2162A | Level Gauge (Reflex) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | VTA | - | - | - | - | - |  | D02 Modified
414 | Lean Glycol Storage Tank | LG-2162B | Level Gauge (Reflex) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | VTA | - | - | - | - | - |  | D02 Modified
415 | Lean Glycol Storage Tank | LG-2162C | Level Gauge (Reflex) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 1.9 | 1.5 | 85 | 50 | VTA | - | - | - | - | - |  | D02 Modified
416 | Lean Glycol Storage Tank | LIT-2162 | Level Indicating Transmitter (DP) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
417 | Lean Glycol Storage Tank | LIT-2161 | Level Indicating Transmitter (DP) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | TK-2102 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
418 | Lean Glycol Storage Tank | PIT-2161 | Pressure Indicating Transmitter (Diaphragm) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | VTA |  | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
419 | Lean Glycol Storage Tank | CC-2162 | Corrosion Coupon (Strip Ladder) | TK-2102 | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER+160mbarg/-7mbarg | 0.1 | 85 | AMB | - | - |  | - | - | -
420 | Lean Glycol Storage Tank | PG-2298 | Pressure Gauge (Bourdon) | TEG-111-0004-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 4 | 0.5 | 85 | 50 | 0-1 barg | - | Barg | - | - | -
421 | Lean Glycol Storage Tank | PG-2163A | Pressure Gauge (Bourdon) | TEG-111-0002-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.1 | 2.07 | 85 | 50 | 0-4 barg | - | Barg | - | - | - |  | D02 Modified
422 | Lean Glycol Storage Tank | PG-2163B | Pressure Gauge (Bourdon) | TEG-111-0006-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0014 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.1 | 2.07 | 85 | 50 | 0-4 barg | - | Barg | - | - | - |  | D02 Modified
423 | Instrument & Plant Air System | PIT-2202 | Pressure Indicating Transmitter (Diaphragm) | PLA-112-0010-AN04-1 1/2"-PT | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 90 | 65 | VTA | 0-18 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
424 | Instrument & Plant Air System | PIT-2201 | Pressure Indicating Transmitter (Diaphragm) | PLA-112-0010-AN04-1 1/2"-PT | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 90 | 65 | VTA | 0-18 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
425 | Instrument & Plant Air System | PCV-2201 | Pressure Control Valve (Globe Valve) | PLA-112-0010-AN04-1 1/2"-PT | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 90 | 65 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
426 | Instrument & Plant Air System | ESOV-2201 | ESD Solenoid Valve | PLA-112-0010-AN04-1 1/2"-PT | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 90 | 65 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | - | D02 Modified
430 | Instrument & Plant Air System | PIT-2203 | Pressure Indicating Transmitter (Diaphragm) | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 85 | 65 | VTA | 0-16 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
431 | Instrument & Plant Air System | PG-2201 | Pressure Gauge (Bourdon) | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 85 | 65 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
432 | Instrument & Plant Air System | PRV-2201 | Pressure Relief Valve | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 85 | 65 | VTA | - | - | - | - | - |  | D02 Modified
433 | Instrument & Plant Air System | PIT-2201A | Pressure Indicating Transmitter (Diaphragm) | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 4.5 | 85 | 65 | VTA | 0-16 barg | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
434 | Instrument & Plant Air System | PIT-2201B | Pressure Indicating Transmitter (Diaphragm) | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 4.5 | 85 | 65 | VTA | 0-16 barg | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
435 | Instrument & Plant Air System | PIT-2201C | Pressure Indicating Transmitter (Diaphragm) | ISA-112-0012-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 4.5 | 85 | 65 | VTA | 0-16 barg | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
436 | Instrument & Plant Air System | PSV-2201 | Pressure Safety Valve | ISA-112-0008-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 4.5 | 85 | 65 | - | - | - | - | - | - | - | D02 Modified
438 | Instrument & Plant Air System | PG-2202 | Pressure Gauge (Bourdon) | V-2203 | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 85 | 65 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
439 | Instrument & Plant Air System | LG-2201 | Level Gauge (Reflex) | V-2203 | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 9 | 85 | 65 | VTA | - | - | - | - | - | - | D02 Modified
443 | Nitrogen Generation System | PG-2211 | Pressure Gauge (Bourdon) | NIT-112-0024-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | 0-16 barg | - | Barg | - | - | -
444 | Nitrogen Generation System | PSV-2211A | Pressure Safety Valve | NIT-112-0022-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | - | - | - | - | - | -
446 | Nitrogen Generation System | PG-2212 | Pressure Gauge (Bourdon) | V-2204 | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | 0-16 barg | - | Barg | - | - | -
447 | Nitrogen Generation System | LG-2211 | Level Gauge (Reflex) | V-2204 | BK-GCS-PEDCO-120-PR-PI-0016 | LIQUID | V-2204 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | VTA | - | - | - | - | -
448 | Nitrogen Generation System | PIT-2213 | Pressure Indicating Transmitter (Diaphragm) | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | VTA | 0-16 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
449 | Nitrogen Generation System | PCV-2211 | Pressure Control Valve (Globe Valve) | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
450 | Nitrogen Generation System | FIT-2211 | Flow Indicating Transmitter (Diaphragm) | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0012 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | - | - | - | FIELD-DCS | AI-IS-R | 4-20 mA
451 | Nitrogen Generation System | FE-2211 | Flow Element (Orifice Plate) | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | - | - | - | - | - | - | -
452 | Nitrogen Generation System | TT-2211 | Temperature Transmitter | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | 0-160 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
453 | Nitrogen Generation System | PIT-2214 | Pressure Indicating Transmitter (Diaphragm) | NIT-112-0021-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | VTA | 0-16 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
454 | Nitrogen Generation System | PIT-2211 | Pressure Indicating Transmitter (Diaphragm) | NIT-112-0024-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0016 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | VTA | 0-16 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
455 | Close Drain System | TG-2221 | Temperature Gauge (Bimetal) | V-2202 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | V-2202 | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 60 | 0-160 °C | - | °C | - | - | - | Note 2
456 | Close Drain System | PG-2221 | Pressure Gauge (Bourdon) | V-2202 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 60 | 0-1 barg | - | Barg | - | - | -
458 | Close Drain System | LG-2221A | Level Gauge (Reflex) | V-2202 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | V-2202 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 60 | VTA | - | - | - | - | - |  | D02 Modified
459 | Close Drain System | LG-2221B | Level Gauge (Reflex) | V-2202 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | V-2202 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 60 | VTA | - | - | - | - | - |  | D02 Modified
460 | Close Drain System | LIT-2221 | Level Indicating Transmitter (DP) | V-2202 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | V-2202 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 60 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
461 | Close Drain System | PIT-2222A | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0032-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.8 | 85 | 5 |  | 0-2 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
462 | Close Drain System | PIT-2222B | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0033-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.8 | 85 | 5 |  | 0-2 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
463 | Close Drain System | PG-2232A | Pressure Gauge (Bourdon) | CDH-112-0033-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 14.5 | 7 | 85 | 5 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
464 | Close Drain System | PG-2232B | Pressure Gauge (Bourdon) | CDH-112-0032-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 14.5 | 7 | 85 | 5 | 0-16 barg | - | Barg | - | - | - |  | D02 Modified
465 | Close Drain System | PG-2222A | Pressure Gauge (Bourdon) | OWA-112-0003-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.5 | 2 | 85 | 50 | 0-1.6 barg | - | Barg | - | - | - |  | D02 Modified
466 | Close Drain System | PG-2222B | Pressure Gauge (Bourdon) | OWA-112-0004-AN01-2"-PT | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.5 | 2 | 85 | 50 | 0-1.6 barg | - | Barg | - | - | - |  | D02 Modified
467 | Close Drain System | LIT-2223 | Level Indicating Transmitter (FLOAT) | SU-2201 | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) | LIQUID | P-2203-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 3.5 | ATM | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
469 | LP Flare System | LIT-2253 | Level Indicating Transmitter (DISPLACER) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
470 | LP Flare System | LIT-2252A | Level Indicating Transmitter (DISPLACER) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
471 | LP Flare System | LIT-2252B | Level Indicating Transmitter (DISPLACER) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
472 | LP Flare System | LIT-2252C | Level Indicating Transmitter (DISPLACER) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 Modified
473 | LP Flare System | TG-2251 | Temperature Gauge (Bimetal) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | GAS | V-2201 | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | 0-100 °C | - | °C | - | - | - | Note 2
474 | LP Flare System | PG-2251 | Pressure Gauge (Bourdon) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | GAS | V-2201 | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | 0-1 barg | - | Barg | - | - | -
475 | LP Flare System | LG-2251 | Level Gauge (Reflex) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | - | - | -
476 | LP Flare System | LIT-2251 | Level Indicating Transmitter (DP) | V-2201 | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | V-2201 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
477 | LP Flare System | PIT-2252 | Pressure Indicating Transmitter (Diaphragm) | FL-112-0004-AN07-10"-PT | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.5 | 85 | 32 | 0-10 barg | 0-1 barg | Barg | - | - | -
478 | LP Flare System | PIT-2251A | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0038-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.6 | 85 | 32 |  | 0-2 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
479 | LP Flare System | PIT-2251B | Pressure Indicating Transmitter (Diaphragm) | CDH-112-0036-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/7.5 | 0.6 | 85 | 32 |  | 0-2 barg | Barg | FIELD-ESD | AI-IS-R | 4-20 mA
480 | LP Flare System | PG-2251A | Pressure Gauge (Bourdon) | CDH-112-0038-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | GAS | P-2201 A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 1.6 | 85 | 32 | 0-4 barg | - | Barg | - | - | - |  | D02 Modified
481 | LP Flare System | PG-2251B | Pressure Gauge (Bourdon) | CDH-112-0037-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 2) | GAS | P-2201 B | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | 1.6 | 85 | 32 | 0-4 barg | - | Barg | - | - | - |  | D02 Modified
482 | Oily Water Sewer | LIT-2273 | Level Indicating Transmitter (FLOAT) | SU-2202 | BK-GCS-PEDCO-120-PR-PI-0021 | LIQUID | SU-2202 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 3.5 | ATM | 85 | AMB | VTA |  | - | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
483 | Fuel Gas System | PG-2271 | Pressure Gauge (Bourdon) | GAS-112-0010-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 48 | 0-10 barg | - | Barg | - | - | - |  | D02 Modified
484 | Fuel Gas System | TG-2271 | Temperature Gauge (Bimetal) | FLG-112-0010-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0002 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 48 | 0-100 °C | - | °C | - | - | - | Note 2 | D02 Modified
485 | Fuel Gas System | CP-2271 | Corrosion Probe (LPR probes) | FLG-112-0010-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 48 | - | - | mm | - | - | - |  | D02 Modified
486 | Fuel Gas System | CC-2271 | Corrosion Coupon (Strip Ladder) | FLG-112-0010-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0014 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 48 | - | - | mm | - | - | - |  | D02 Modified
487 | Fuel Gas System | FG-2272 | Rotameter | FL-112-0040-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | ATM | 85 | AMB | - | - | - | - | - | - |  | D02 Modified
488 | Fuel Gas System | PG-2274 | Pressure Gauge (Bourdon) | FL-112-0040-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 48 | 0-10 barg | - | Barg | - | - | - |  | D02 Modified
489 | Fuel Gas System | EZSC-2272 | Limit Switch Close (Included in ON-OFF Valve) | GAS-111-0004-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
490 | Fuel Gas System | EZSO-2272 | Limit Switch Open (Included in ON-OFF Valve) | GAS-111-0004-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
491 | Fuel Gas System | ESOV-2272 | ESD Solenoid Valve | GAS-111-0004-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
492 | Fuel Gas System | ESDV-2272 | Emergency Shut Down Valve (Ball Valve) | GAS-111-0004-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | - | - | - | - | - | - | -
493 | Fuel Gas System | PIT-2272 | Pressure Indicating Transmitter (Diaphragm) | FLG-112-0006-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | VTA | 0-10 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
494 | Fuel Gas System | PCV-2272 | Pressure Control Valve (Globe Valve) | FLG-112-0006-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | DCS | BK-GCS-PEDCO-120-IN-DT-0011 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | - | - | - | DCS-FIELD | AO-IS-R | 4-20 mA
495 | Fuel Gas System | PG-2272 | Pressure Gauge (Bourdon) | GAS-111-0004-AN07-3"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 5.1 | 85 | 36.9 | 0-10 barg | - | Barg | - | - | -
496 | Fuel Gas System | PDG-2271 | Differential Pressure Gauge (Diaphragm) | V-2205 | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | VTA | 0-1 bara | Bar | - | - | -
497 | Fuel Gas System | LIT-2272 | Level Indicating Transmitter (DISPLACER) | V-2205 | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | V-2205 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | VTA | - | - | FIELD-ESD | AI-IS-R | 4-20 mA |  | D02 MODIFIED
498 | Fuel Gas System | LG-2271 | Level Gauge (Reflex) | V-2205 | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | V-2205 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | VTA |  | - | - | - | -
499 | Fuel Gas System | LIT-2271 | Level Indicating Transmitter (DISPLACER) | V-2205 | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | V-2205 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | VTA |  | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 MODIFIED
500 | Fuel Gas System | PG-2273 | Pressure Gauge (Bourdon) | V-2205 | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | 0-10 barg |  | Barg | - | - | -
501 | Fuel Gas System | XZSC-2271 | Limit Switch Close (Included in ON-OFF Valve) | CDH-112-0039-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
502 | Fuel Gas System | XZSO-2271 | Limit Switch Open (Included in ON-OFF Valve) | CDH-112-0039-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
503 | Fuel Gas System | PSOV-2271 | Process Solenoid Valve | CDH-112-0039-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | - | - | - | DCS-FIELD | DO-NIS-NR | 24 VDC
504 | Fuel Gas System | ESOV-2271 | ESD Solenoid Valve | CDH-112-0039-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | - | - | - | ESD-FIELD | DO-NIS-R | 24VDC LOOP POWER | -
505 | Fuel Gas System | XV-2271 | ON/OFF VAVLE (Ball Valve) | CDH-112-0039-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 36.7 | - | - | - | - | - | - | -
506 | Fuel Gas System | FG-2271 | Rotameter | CHM-112-0020-AS00-3/4"-NP | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 9 | ATM | 55 | AMB | - | - | - | - | - | -
507 | Fuel Gas System | PIT-2271 | Pressure Indicating Transmitter (Diaphragm) | FLG-112-0106-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 33.6 | VTA | 0-10 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA
508 | Fuel Gas System | TIT-2271 | Temperature Indicating Transmitter (RTD) | FLG-112-0106-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0005 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 33.6 | 0-100 °C | - | °C | FIELD-DCS | AI-IS-R | 4-20 mA | Note 2
509 | Fuel Gas System | FE-2271 | Flow Element (Orifice Plate) | FLG-112-0106-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0013 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 33.6 | - | - | - | - | - | -
510 | Fuel Gas System | FIT-2271 | Flow Indicating Transmitter (Diaphragm) | FLG-112-0106-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0012 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 33.6 | - | - | - | FIELD-DCS | AI-IS-R | 4-20 mA
511 | Fuel Gas System | PSV-2271 | Pressure Safety Valve | FLG-111-0011-AN07-2"-PT | BK-GCS-PEDCO-120-PR-PI-0022 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | F.V/9 | 4.9 | 85 | 33.6 | - | - | - | - | - | -
514 | DIESEL OIL SYSTEM | PG-2281 | Pressure Gauge (Bourdon) | V-2206A | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | 0-1 barg | - | Barg | - | - | -
515 | Fire Water Diesel Oil Drum | LIT-2281 | Level Indicating Transmitter (DP) | V-2206A | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | LIQUID | V-2206 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
516 | Fire Water Diesel Oil Drum | LG-2281 | Level Gauge (Reflex) | V-2206A | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | LIQUID | V-2206 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | VTA | - | - | - | - | - |  | D02 Modified
517 | Fire Water Diesel Oil Drum | PG-2282 | Pressure Gauge (Diaphragm) | Discharge P-2206A | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.1 | 0.95 | 85 | 50 | 0-1.6 barg | - | Barg | - | - | - |  | D02 Modified
518 | Fire Water Diesel Oil Drum | PG-2283 | Pressure Gauge (Bourdon) | Charge P-2206A | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.11 | 85 | 50 | 0-1 barg | - | Barg | - | - | - |  | D02 Modified
519 | Fire Water Diesel Oil Drum | TSV-2281 | Temperature Safety Valve | DO-112-0005A-AN01-1"-PT DO-112-0006A-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0023 (1 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.1 | 0.95 | 85 | AMB | - | - | - | - | - | - |  | D02 Modified
520 | Diesel Generator Diesel Oil Drum | PG-2281B | Pressure Gauge (Bourdon) | V-2206B | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | 0-1 barg | - | Barg | - | - | - |  | D02 Modified
521 | Diesel Generator Diesel Oil Drum | LIT-2281B | Level Indicating Transmitter | V-2206B | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | LIQUID | V-2206 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
522 | Diesel Generator Diesel Oil Drum | LG-2281B | Level Gauge (Reflex) | V-2206B | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | LIQUID | V-2206 | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | VTA | - | - | - | - | - |  | D02 Modified
523 | Diesel Generator Diesel Oil Drum | PG-2282B | Pressure Gauge (Diaphragm) | Discharge P-2206B | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.1 | 0.95 | 85 | 50 | 0-1.6 barg | - | Barg | - | - | - |  | D02 Modified
524 | Diesel Generator Diesel Oil Drum | PG-2283B | Pressure Gauge (Bourdon) | Charge P-2206B | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.11 | 85 | 50 | 0-1 barg | - | Barg | - | - | - |  | D02 Modified
525 | Diesel Generator Diesel Oil Drum | TSV-2261B | Temperature Safety Valve | DO-112-0005B-AN01-1"-PT DO-112-0006B-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0023 (2 of 2) | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.5 | ATM | 85 | AMB | - | - | - | - | - | - |  | D02 Modified
526 | Potable Water System | LIT-2291 | Level Indicating Transmitter (DP) | TK-2209 | BK-GCS-PEDCO-120-PR-PI-0024 | LIQUID | TK-2209 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM+FULL OF WATER | ATM | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-NR | 4-20 mA |  | D02 Modified
527 | Potable Water System | PG-2291 | Pressure Gauge (Bourdon) | PTW-112-0003-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0024 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.8 | 1.95 | 85 | AMB | 0-4 barg | - | Barg | - | - | - |  | D02 Modified
528 | Potable Water System | PG-2292 | Pressure Gauge (Diaphragm) | PTW-112-0001-AZ00-2"-NP | BK-GCS-PEDCO-120-PR-PI-0024 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.65 | 0.15 | 85 | AMB | 0-1 barg | - | Barg | - | - | -
529 | Glycol Sump Drum | PRV-2291 | Pressure Relief Valve | NIT-112-0005-AN01-1"-PT | BK-GCS-PEDCO-120-PR-PI-0025 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 12.5 | 8 | 85 | 60 | VTA | - | - | - | - | -
530 | Glycol Sump Drum | PG-2295 | Pressure Gauge (Bourdon) | NIT-111-0009-AN04-1"-PT | BK-GCS-PEDCO-120-PR-PI-0025 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 4 | 0.5 | 85 | AMB | 0-1 barg | - | Barg | - | - | -
531 | Glycol Sump Drum | PRV-2292 | Pressure Relief Valve | NIT-111-0009-AN04-1"-PT | BK-GCS-PEDCO-120-PR-PI-0025 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.1 | 85 | AMB | VTA | - | - | - | - | -
532 | Glycol Sump Drum | PSV-2293 | Pressure Saftey Valve | TEG-111-0113-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0025 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0009 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.5 | 0.1 | 85 | AMB | VTA | - | - | - | - | -
533 | Glycol Sump Drum | PG-2293 | Pressure Gauge (Bourdon) | TEG-111-0011-AN04-2"-PT | BK-GCS-PEDCO-120-PR-PI-0025 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 2.6 | 2.1 | 85 | AMB | 0-4 barg | - | Barg | - | - | -
534 | Glycol Sump Drum | PIT-2191 | Pressure Indicating Transmitter (Diaphragm) | V-2107 | BK-GCS-PEDCO-120-PR-PI-0025 | LIQUID | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.1 | 85 | AMB |  | 0-0.2 barg | Barg | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
535 | Glycol Sump Drum | LIT-2293 | Level Indicating Transmitter (DP) | V-2107 | BK-GCS-PEDCO-120-PR-PI-0025 | LIQUID | V-2205 | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.1 | 85 | AMB | VTA | - | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
536 | Glycol Sump Drum | PG-2294 | Pressure Gauge (Bourdon) | V-2107 | BK-GCS-PEDCO-120-PR-PI-0025 | GAS | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 3.6 | 0.1 | 85 | AMB | 0-1 barg | - | Barg | - | - | -
537 | Fire Water System | PG-2301 | Pressure Gauge (Bourdon) | FWA-113-0001-AN04-3"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
538 | Fire Water System | ZSC-2301 | Limit Switch Close (Included in ON-OFF Valve) | FWA-112-0007-AN04-3"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 1.5 | 1 | 85 | 5-55 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC
539 | Fire Water System | ZSO-2301 | Limit Switch Open (Included in ON-OFF Valve) | FWA-112-0007-AN04-3"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | 1.5 | 1 | 85 | 5-55 | - | - | - | FIELD-DCS | DI-NIS-NR | 24 VDC | -
540 | Fire Water System | XV-2301 | ON/OFF VAVLE (Ball Valve) | FWA-112-0007-AN04-3"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0010 | BK-GCS-PEDCO-120-IN-DG-0003 | - | BK-GCS-PEDCO-120-IN-PY-0004 | 1.5 | 1 | 85 | 5-55
541 | Fire Water System | LG-2301 | Level Gauge (Float) | TK-2301-A | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | VTA |  | - | - | - | -
542 | Fire Water System | LIT-2301 | Level Indicating Transmitter (DP) | TK-2301-A | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | TK-2301-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | VTA |  | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
543 | Fire Water System | LSLL-2301 | Level Switch Low Low (Float) | TK-2301-A | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL |  | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | - | - | - | F&G | DI-NIS-R | 24 VDC
544 | Fire Water System | LG-2302 | Level Gauge (Float) | TK-2301-B | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0003 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | VTA |  | - | - | - | -
545 | Fire Water System | LIT-2302 | Level Indicating Transmitter (DP) | TK-2301-B | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | TK-2301-A | BK-GCS-PEDCO-120-IN-DT-0006 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0005 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | VTA |  | - | FIELD-DCS | AI-IS-R | 4-20 mA |  | D02 Modified
546 | Fire Water System | LSLL-2302 | Level Switch Low Low (Float) | TK-2301-B | BK-GCS-PEDCO-120-SA-PI-0001 (1 of 2) | Fire Water | LOCAL |  | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 | ATM | ATM | 85 | 5-55 | - | - | - | F&G | DI-NIS-R | 24 VDC
547 | Fire Water System | PT-2301 | Pressure Transmitter | FWA-113-0025-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0004 | BK-GCS-PEDCO-120-IN-DG-0002 | BK-GCS-PEDCO-120-IN-DG-0004 | BK-GCS-PEDCO-120-IN-PY-0003 |  |  |  |  | - | - | - | F&G | DI-NIS-R | 24 VDC
548 | Fire Water System | PG-2303A | Pressure Gauge (Bourdon) | FWA-113-0026-AN04-2"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2302A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
549 | Fire Water System | PG-2304A | Pressure Gauge (Bourdon) | Discharge P-2302A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2302A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
550 | Fire Water System | PG-2303B | Pressure Gauge (Bourdon) | FWA-113-0027-AN04-2"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2302B | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
551 | Fire Water System | PG-2304B | Pressure Gauge (Bourdon) | Discharge P-2302B | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2302B | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
552 | Fire Water System | PG-2304 | Pressure Gauge (Bourdon) | FWA-113-0018-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2302B | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg
553 | Fire Water System | PG-2305 | Pressure Gauge (Bourdon) | FWA-113-0025-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg | [6 empty] | D02 Modified
554 | Fire Water System | FG-2301 | Rotameter | FWA-113-0007-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | LOCAL | BK-GCS-PEDCO-120-IN-DT-0018 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 |  |  |  | - | - | -
555 | Fire Water System | PG-2301A | Pressure Gauge (Bourdon) | FWA-113-0020-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2301A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
556 | Fire Water System | PG-2302A | Pressure Gauge (Bourdon) | Discharge P-2301A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2301A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
557 | Fire Water System | PG-2301B | Pressure Gauge (Bourdon) | FWA-113-0019-AN04-12"-PT | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2301A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
558 | Fire Water System | PG-2302B | Pressure Gauge (Bourdon) | Discharge P-2301A | BK-GCS-PEDCO-120-SA-PI-0001 (2 of 2) | Fire Water | P-2301A | BK-GCS-PEDCO-120-IN-DT-0001 | BK-GCS-PEDCO-120-IN-DG-0002 | - | BK-GCS-PEDCO-120-IN-PY-0003 | 16.5 | 11 | 85 | 5-55 | 0-25 barg |  | Barg | - | - | -
D02
Note on C492: Arefe Khajevand: