## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DG-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1092 |  |  | Transmital Date: 19 Jun 2022
Document Title: Instrument & F&G Junction Box Termination Diagram |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1092 |  |  | Transmital Date: 19 Jun 2022
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-DG-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مدارک زیر به عنوان مدرک مرجع ذکر گردند : Panels & Junction Box List Instrument and F&G Cable List |  | 01/2294/183561 | 1401/05/27 | با توجه به اینکه مدرک ذکر شده توسط کارفرمای محترم (Panels & Junction Box List ) خود نوسط مدرک Instrument & F&G Junction Box Termination Diagram تهیه میشود بنابراین به عنوان مرجع ذکر نمی شود. مدرک Instrument and F&G Cable List به عنوان مرجع در نظر گرفته شد.
2 | متن فارسی فایل اصلی مدرک ناخوانا می باشد ، فونت فارسی مورد استفاده به همراه مدرک ارسال گردد. |  | 01/2294/183561 | 1401/05/27 | کارفرمای محترم با توجه به این که تمام مدارک به همراه فایل pdf ارسال میشوند ، فایل pdf آن مورد بررسی قرار گیرد.
3 | در صفحات 7 و 8 ، note 2 اصلاح گردد : سیگنال های ورودی و خروجی این صفحه به سیستم کنترل/ESD جدید و در پنل های موجود وصل میگردد همچنین جداسازی سیگنال های ESD از سیگنال های کنترل الزامی می باشد. |  | 01/2294/183561 | 1401/05/27 | با نوجه به نظر کارفرمای محترم مدرک اصلاح گردید.
4 | این مدارک مطابق تغییرات مدارک مرجع بروز رسانی گردد. |  | 01/2294/183561 | 1401/05/27 | با نوجه به نظر کارفرمای محترم و آخرین نسخه از مدارک مرجع، مدرک اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 26 Jul 2022 |  |  |  |  | Date: