## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | LI | 0007 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | FEB.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | SEP.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708008
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از6
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0007 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X |  |  | X |  |  |  | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X |  |  | X |  |  |  | 69
6 |  | X | X |  | X |  |  |  | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCES
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از6
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | LI | 0007 | D03
REFERENCE DOCUMENTS:
| I/O LIST FOR CONTROL SYSTM-EXTENTION OF BINAK BK MANIFOLD | [8 empty] | BK-W007S-PEDCO-110-IN-LI-0002
| I/O LIST FOR ESD SYSTEM-EXTENTION OF BINAK BK MANIFOLD | [8 empty] | BK-W007S-PEDCO-110-IN-LI-0003
| I/O LIST FOR F&G SYSTEM-EXTENTION OF BINAK BK MANIFOLD | [8 empty] | BK-W007S-PEDCO-110-IN-LI-0004
| SPECIFICATION FOR INSTRUMENTATION | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| SPECIFICATION FOR CONTROL SYSTEM | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0002
| SPECIFICATION FOR ESD SYSTEM | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0003
| SPECIFICATION FOR ESD SYSTEM | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0012
| SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM(PU | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0004
| BLOCK DIAGRAM CONFIGURATION FOR CONT./ESD/F&G SYS. - EXT. OF BINAK B/C MANI. | [8 empty] | BK-W007S-PEDCO-110-IN-DG-0001
D03

## 110VAC_UPS
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 4 از6
9184 – 073 - 053 |  |  |  | BK | W007S |  | PEDCO | 110 |  | IN | LI |  | 0007 |  | D03
INST./CONTROL UPS 110 VAC POWER CONSUMPTION TABLE
- Table (1) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE3) |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (KW)
| 1 | DCS ( SYSTEM & MARSHALING ) PANEL (INCLUDING NETWORK SWITCHES) |  |  | 1 | 2 hr. | 42 |  | 1 |  |  | 2 Nos. (Redundant) |  | 1
| 2 | ESD ( SYSTEM & MARSHALING ) PANEL |  |  | 1 | 2 hr. | 18 |  | 0.7 |  |  | 2 Nos. (Redundant) |  | 0.7
| 3 | OPERATOR WORKSTATION (INCLUDING DCS, ESD) |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
| 4 | DCS ENGINEERING WORKSTATION |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
| 5 | ESD ENGINEERING WORKSTATION |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
| 6 | PRINTERS (Note 2) |  |  | 1 ( Note 2) | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
|  |  | TOTAL POWER CONSUMPTION (KW) | [10 empty] | 4.1
|  |  | TOTAL POWER CONSUMPTION (KW) + 20 % SPARE | [10 empty] | 4.92
|  |  | ADDITIONAL POWER CONSUMPTION REQUIRED FOR EXISTING SYSTEMS (DUE TO CLIENT REQUEST NOTE 5) | [10 empty] | 1
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW) | [10 empty] | 5.92
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2 : Printers Are Not Working In The Same Time. Note 3 : Power Consumption of panels have been estimatted considering project I/O count. Refer to ''I/O List For Control System - Extension of Binak B/C Manifold Doc.No.BK-W007S-PEDCO-110-IN-LI-0002 , I/O List For ESD System - Extension of Binak B/C Manifold Doc.No.BK-W007S-PEDCO-110-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0004''. Note 4: Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be considered in UPS battery sizineg by electrical . Note 5: Through 110 VAC to 24 VDC convertor which shall be provided by UPS vendor. According to IPS-E-IN-180 (first edition may 2013) part 6.1, back up time for additional power consumption required for existing system shall be considered 2 hours.
D03
D03
D03
D03
D03
D03
D03
D03
D03

## 230VAC-NON UPS
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از6
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | LI | 0007 | D03
INST./CONTROL NON- UPS 230 VAC POWER CONSUMPTION TABLE
- Table (2) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room.
| ITEM | DESCRIPTION |  |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  |  |  | QTY. (Note 1) | TOTAL POWER CONSUMPTION (KW)
| 1 | CABINET UTILITIES FOR PCS (HEATER, SOCKET, FAN , LIGHT) |  |  | 0.16 |  |  |  |  | 1 | 0.16
| 2 | CABINET UTILITIES FOR ESD (HEATER, SOCKET, FAN , LIGHT) |  |  | 0.16 |  |  |  |  | 1 | 0.16
| 3 | CONTROL DESK SOCKETS |  |  | 0.5 |  |  |  |  | 3 | 1.5
| TOTAL POWER CONSUMPTION | [9 empty] | 1.82
|  |  | TOTAL POWER CONSUMPTION (KW) | [7 empty] | 1.82
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW) | [7 empty] | 2.184
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents.
Note 2 : Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be
considered in UPS battery sizineg by electrical .
D03
D03

## 24 VDC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I&C POWER CONSUMPTION SUMMARY - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه | شماره صفحه: 6 از6
9184 – 073 - 053 |  |  |  | BK | W007S |  | PEDCO | 110 |  | IN | LI |  | 0007 |  | D03
INST./CONTROL UPS 24 VDC POWER CONSUMPTION TABLE
- Table (3) is represents 24 DC UPS power consumption for FACP system and related detectors. The estimation is based on the design of FACP systems, comprising of various equipment located in Control Room/Electrical room.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION FOR QUIESENCE MODE(KW) |  |  | TOTAL POWER CONSUMPTION FOR ALARM MODE (KW)
| 1 | FACP system |  |  | 1 No. | 24hr. | 54 |  | 0.4 ( for Quiescence& Alarm mode) |  |  | 2 Nos. (Redundant) |  | 0.4+(0.02 x 54) = 1.48 KW for 24hr (Note 3) |  |  | -
| 2 | FACP Detectors |  |  | 54 No. (Note 5) | 24hr. |  |  | 0.02 (for Quiescence mode)
[6 empty] | 5 Min |  |  | 0.2 (for alarm mode) |  |  |  |  | - |  |  | 0.4+(0.2 x11) = 2.6 KW for 5 Min (Note 3,5)
|  |  | TOTAL POWER CONSUMPTION FOR 5 Min BACK UP TIME (KW) | [10 empty] | 2.6 (Note 3)
|  |  | TOTAL POWER CONSUMPTION FOR 5 Min BACK UP TIME (KW) + 20 % SPARE | [10 empty] | 3.12 (Note 3)
|  |  | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME (KW) | [10 empty] | 1.48 (Note 3)
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW)+ 20 % SPARE | [10 empty] | 1.776 (Note 3)
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be considered by electrical . Note 3: DC charger shall supply 2.6 KW + Spare, for 24H back up time but also it shall be capable to prepare 1.48 KW+ Spare, as a peak power consumption in alarming conditions for 5 Min back up time. it shall be considered during battery sizing in related documents. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to ''I/O List For Control System - Extension of Binak B/C Manifold Doc.No.BK-W007S-PEDCO-110-IN-LI-0002 , I/O List For ESD System - Extension of Binak B/C Manifold Doc.No.BK-W007S-PEDCO-110-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0004. Note 5: Twenty percent of detectors (11 No. of 54 No.) are amounted to work in the same time during alarm mode.
D03