## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0007 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1439 |  |  | Transmital Date: 26 Sep 2022
Document Title: I&C Power Consumption Summary |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-T-1439 |  |  | Transmital Date: 26 Sep 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-LI-0007_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comment
1 | لازم است جزئیات محاسبات ، لیست ادوات (شامل کارت ها ، مبدل ها ، سلونوییدها و ...)، تعداد و مصارف تجهیزات به تفکیک بیان شده و مدرک بر این مبنا مرود بازنگری و اصلاح کلی قرار گیرد. |  | 01/2294/296323 | 1401/8/14 | مبنای محاسبات بر اساس تعدادI/O با توجه به مدارک سازندگان در پروژه های مشابه میباشد که تمام سلونویید ها و ادوات لحاظ شده را شامل میشود. تفکیک جدول براساس تابلوی سیستمی و مارشالینک ارائه شده که معادل یونیت تغذیه پیش بینی شده توسط سازندگان برای تابلوهای مشابه در پروژه های در دست ساخت این شرکت میباشد.
2 | پنل های کنترل و ESD از UPS 110VAC Dual Redundant تغذیه گردد. |  | 01/2294/296323 | 1401/8/14 | در صفحه 4 مدرک ، پنل های کنترل و ESD به صورت UPS 110VAC Dual Redundant در نظر گرفته شده اند.
3 | پنل FACP از برق 24 ولت DC با پشتیبانی 24 ساعت در حالت استند بای و بعد از آن 5 دقیقه در حالت آلارم تغذیه گردد. |  | 01/2294/296323 | 1401/8/14 | با توجه به نظر کارفرمای محترم ، قابل ذکر است که در صفحه 6 مدرک دقیقا با همین نکته (برق پنل FACP ، 24 ولت DC با پشتیبانی24H+5M) در نظر گرفته شده است و همچنین با توجه به آخرین نسخه مدارک مرجع ، مدرک اصلاح گردید.
لازم به ذکر است که صورت جلسه ی جانمایی دستگاه های شارژر و UPS پروژه در ساختمان های کلاستر بینک مورخ 1401/8/24 و نامه ی شماره 01/2290/412545 مورخ 1401/10/28 که به پیوست موجود است ، در ارائه این مدرک لحاظ شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: