## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0001-D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1193 |  |  | Transmital Date: 25-Jul-2022
Document Title: Electrical Load List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1193 |  |  | Transmital Date: 25-Jul-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-LI-0001-D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ردیف 30 و31، فیدرهای مربوط به پمپ های جوکی به لحاظ الزامات ایمنی می بایست بر روی باس اضطراری قرار گیرد. |  | 1401-2294-183483 | 1401-05-27 | اعمال گردید.
2 | ردیف 77، توان در نظر گرفته شده برای این آیتم مربوط به سیستم تهویه سوییچگیر، کم در نظر گرفته شده است. مقدار آن می بایست بر اساس توان واقعی دستگاههای تهویه متمرکز اصلاح گردد. |  | 1401-2294-183483 | 1401-05-27 | محاسبات سیستم تهویه مجددا مورد بازنگری قرار گرفت و این اعداد در مدرک لیست بار لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 06-Aug-22 |  |  |  |  | Date: