## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-TB-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1416 |  |  | Transmital Date: 19 sep 2022
Document Title: TBE/TBA For Control Valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1416 |  |  | Transmital Date: 19 sep 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-TB-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | دقت شود طول مدت ساخت در بازه زمانی پروژه قرار داشته باشد. |  | 01/2294/267237 | 1401/07/25 | زمان ساخت در تمامی پروپوزالها اشاره گردیده و سازنده ای به عنوان سازنده نهایی انتخاب می گردد که تمامی شرایط از جمله زمان ساخت مناسب با بازه زمانی پروژه را داشته باشد.
2 | سایز کنترل ولو در جدول ارزیابی 3 اینچ ذکر گردیده در صورتی که در مدارک پیوست سایزهای مختلفی از طرف سازندگان در نظر گرفته شده است، شفاف سازی شود. |  | 01/2294/267237 | 1401/07/25 | مطابق با IPS-E-In-160 پاراگراف 7.2.11 : : Control valves installed in pipe lines should normally be at least one pipe size smaller than the computed line size. لذا سایز کنترل ولو حداقل باید یک سایز کوچکتر از سایز خط باشد ولی در صورتیکه سایزینگ سازنده تا نصف خط هم مطابق استاندارد پاسخ دهد، قابل پذیرش است. همانطور که کارفرمای محترم هم مستحضر هستند، در مدرک دیتا شیت مقابل عدد 3" عبارت ( VTC) به معنای تایید سازنده نیز آورده شده است.
3 | کلاس نشتی شیرها مطابق Spec و اصول طراحی مورد بازنگری قرار گیرد. |  | 01/2294/267237 | 1401/07/25 | مطابق با SPEC پروژه با توجه به آنکه شیرهای پروژه به صورت single seated control valve هستند، کلاس نشتی آنها برابر با کلاس IV در نظر گرفته شده است.
4 | نوع Position Switch مطابق Spec مورد بازنگری قرار گیرد. |  | 01/2294/267237 | 1401/07/25 | کنترل ولوهای مورد اشاره با توجه به عدم نیاز پروژه، فاقد Position Switch و Solenoid می باشند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and inculpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  |  | Signature
| Date: 10 Jan 2022 |  |  |  |  | Date: