## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DG-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1426 |  |  | Transmital Date: 20 Sep 2022
Document Title: F&G System Loop Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1426 |  |  | Transmital Date: 20 Sep 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-NISOC-110-IN-DG-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نحوه اتصال انواع تجهیزات F&G در صفحه اختصارات و علائم نمایش داده شود. |  | 01-2294-296325 | 1401/08/14 | شکل اختصاری نشان داده شده شامل همه ادوات به لحاظ اتصالات الکتریکی میشود. این ادوات با مشخصه tag در صفحات مدرک با جزئیات نشان داده شده اند. در صورتی که مورد خاصی مد نظر کارفرمای محترم است لطفا به طور خاص ذکر شود.
2 | نحوه اتصال انواع تجهیزات F&G در لوپ نمایش داده شود. (قاعدتا نحوه اتصال تجهیزات دیداری، شنیداری و دتکتور و ... مشابه هم نیستند.) |  | 01-2294-296325 | 1401/08/14 | تمام تجهیزات اعم از دیداری ، شنیداری و دتکتور و .... برای فضای اتاق طراحی شده اند وهمگی از نوع آدرس پذیر هستند و Loop Chain Connection میباشند. لازم به ذکراست مطابق تجیزات موجود در بازار امکان اتصال تجهیزات دیداری، شنیداری همراه با بقیه دتکتورها در یک لوپ می باشد.
3 | NOTE ها متناسب مدرک F&G اصلاح گردند. |  | 01-2294-296325 | 1401/08/14 | مطابق خواست کارفرمای محترم اصلاح شد.
4 | اتصال سریال به سیستم کنترل DCS نمایش داده شود. |  | 01-2294-296325 | 1401/08/14 | مطابق مدرک I/O List For F&G Systems - Extension of Binak B/C Manifold ارتباطی با سیستم DCS ندارد.
5 | آدرس دهی تجهیزات و شماره ترمینال ها با توجه به مدارک سازنده به روز رسانی گردد. |  | 01-2294-296325 | 1401/08/14 | با توجه به آخرین نسخه مدارک ، اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 19 Sep 2022 |  |  |  |  | Date: