## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DG-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1426 |  |  | Transmital Date: 20 Sep 2022
Document Title: F&G System Loop Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-1426 |  |  | Transmital Date: 20 Sep 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DG-0007_D00 |  |  | Comment Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05867 | 2022-10-10 | ملاحظه گردید.
2 | اين مدرك با مدرك پيش نياز F&G location Layout تناقض دارد براي مثال MAC-2304 |  | BK-SUR-ENG-INS-01-05867 | 2022-10-10 | مطابق اخرین نسخه از مدارک مرجع اصلاح شد.
3 | با توجه به اينكه مدارك پيشين بر روي اين مدرك نهايي نيست در صورت هر گونه تغيير موارد در اين مدرك مشخص شود. |  | BK-SUR-ENG-INS-01-05867 | 2022-10-10 | مطابق اخرین نسخه از مدارک مرجع اصلاح شد.
4 | بازگشت به كامنت شماره يك مدرك پيشين، لزوم وجود Action در نتيجه استفاده از سيستم Voting براي H2 Detector در اتاق باطري بررسي گردد. |  | BK-SUR-ENG-INS-01-05867 | 2022-10-10 | با توجه به مدرک ESD HIERARCHY هیچ ESD ACTION از H2 Detector موجود در اتاق باطري دریافت نمی شود در نتیجه نیاز به درنظر گرفتن سیستم Voting برای این تجهیزات نمی باشد. لازم به ذکر است این مدرک مطابق مدرک F&G LOC. LAYOUT - EXT. OF BINAK BC MANتهیه شده است.
5
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 10 Oct 2022 |  |  |  |  | Date: