## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0002-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1292 |  |  | Transmital Date: 20-Aug-2022
Document Title: LV Switchgear/MCC Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1292 |  |  | Transmital Date: 20-Aug-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0002-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پیرو نامه شماره 183483 مورخ 27/05/1401، لازم است تغذیه هر دو عدد الکتروپمپ جوکی از باس اضظراری انجام گیرد. لذا این مدرک بر اساس آخرین ویرایش لیست بار تأییدی این امور اصلاح گردد. |  | 1401-2294-216125 | 1401-06-17 | پمپهای جوکی بر روی باسبار اضطراری قرار گرفته است.
2 | با توجه به مشخص نشدن توان و وضعیت سیستم تهویه کلیدخانه موجود لازم است که هر چه سریعتر موضوع تعیین تکلیف گردد. |  | 1401-2294-216125 | 1401-06-17 | توان در نظر گرفته شده در این مدرک بر اساس آخرین لیست بارهای HVAC می باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Gh.Saadatian | Signature |  |  |  | Clarified By: | Signature
| Date: 28-Aug-22 |  |  |  |  | Date: