## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-PR-DG-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1050 |  |  | Transmital Date: 6/7/2022
Document Title:Cause & Effect Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1050 |  |  | Transmital Date: 6/7/2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-PR-DG-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مقتضی است ضمن اعمال نقطه نظرات قبلی این امور بر مدارکد P&ID و ESD Philosophy و ESD Logic Diagram مدرک ارسالی بازنگری،اصلاح و تکمیل گردد. |  | 1401-2294-144345 | 1401/04/28 | اعمال گردید.
1 | مقتضی است شماره P&ID و Tag Number تجهیزات و Alarm Tag مربوطه به مدرک اضافه گردد. |  | 1401-2294-144345 | 1401/04/28 | اعمال گردید.
1 | جهت سیگنال های Power Failure(ESD1) ، UPS Failure (ESD0) ، Control System Failure ، Instrument Low Pressure(ESD0) (ESD0) ، سطح ESD در نظر گرفته شود. ESD 0 (Plant Shutdown With Depressurizing) ESD1 ( Plant Shutdown Without Depressurizing) |  | 1401-2294-144345 | 1401/04/28 | سطح ESD-0 تحت عنوان PLANT SHUTDOWN WITH DEPRESSURIZING و ESD-1 تحت عنوان EACH FLOW LINE SHUT DOWN WITHOUT DEPRESSURIZING تعریف شده است. UPS FAILERE و LOW/HIGH PRESSURE AT EACH FLOW LINE در مدرک فوق تعریف شده است. در ارتباط با POWER FAILURE و SYSTEM FAILURE لازم به ذکر است که علت های فوق در محدوده کاری این مشاور نبوده و دستور های فوق از سیستم کنترلی موجود دریافت شده و متعاقبا اقدامات لازم با آن صورت می پذیرد.
| در صورت وجود سیستم حفاظتی Exist ارتباط سیستم های New و موجود در نظر گرفته شود. |  | 1401-2294-144345 | 1401/04/28 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: