## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0001-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0966 |  |  | Transmital Date: 17-May-2021
Document Title: Electrical Overall Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0966 |  |  | Transmital Date: 17-May-2021
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0001-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised according to comments on MV/LV single line diagram and load list (If required). |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | با توجه به آخرین تغییرات مدرک تک خطی این مدرک بروزرسانی گردید. |  |  | Noted and Closed.
2 | Rated current of emergency busbar shall be same as normal bus bar current. (2000A) |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | اعمال گردید. |  |  | Noted and Closed.
3 | Interlock between main incoming from 11/0.42KV transformer, emergency bus tie and DG circuit breaker shall be shown. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | با توجه به اینکه مدرک مذکور نحوه ی برق رسانی را نمایش می دهد،لذا اینترلاک مربوط در مدارک اسکماتیک نمایش داده شده است. |  |  | See below item 10.
4 | The rated voltage of Diesel Generator shall be modified to 400V instead of 380V. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | اعمال گردید. |  |  | Noted and Closed.
5 | Following items shall be specified for VCB and ACB: -Rated Current -No. of Poles |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | جریان نامی برای کلیدهای MV اضافه گردید،خروجی های LV نیز مطابق با مدرک اسکماتیک نشان داده شده است که در آن تعداد پل های کلید مشخص است. |  |  | Noted and Closed.
6 | According to LV logic diagram, the status of emergency incoming CB. Shall be modified to NC. Meanwhile the status of DG circuit breaker shall be modified to NO. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | مطابق با کامنت های پیشین کارفرمای محترم کلید موجود در پنل کنترلی دیزل ژنراتور(QDG) به صورت NC در مدارک اسکماتیک و تک خطی در نظر گرفته شده است،حال آنکه در مدرک لاجیک دیاگرام که مطابق با تابلو های موجود ایستگاه می باشد،شرط وصل کلید (QDG) ، استارت و گردش به کار دیزل ژنراتور می باشد، لذا نیاز می باشد این موضوع شفاف سازی گردد. |  |  | See below item 11.
7 | Size of capacitor banks for fire fighting pump shall be added. Meanwhile the location shall be modified base on comments on LV single line diagram. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | پیرو تماس تلفنی و با توجه به اینکه در مواقع آتشسوزی پمپ فعال می گردد ،پیشنهاد می گردد از خازن گذاری صرف نظر گردد. |  |  | Noted and Closed.
8 | Size of capacitor banks shall be modified base on comments on capacitor bank sizing document. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | اعمال گردید. |  |  | Noted and Closed.
9 | Box symbol for spare feeders shall be deleted in 11KV switchgear. |  | BK-SUR-ENG-ELE-00-02907 | 2022-02-01 | اعمال گردید. |  |  | Noted and Closed.
10 | See above item 3: According to NISOC comment, transfer system (Connection between incoming, Emergency coupler and QDG) shall be completely shown. |  | BK-SUR-ENG-ELE-01-04067 | 2022-04-26 | اعمال گردید. |  |  | Noted and Closed.
11 | See above item 6: According to our telephone conversation status of DGCB and related incoming LV switchgear shall be modified base on NISOC comment. |  | BK-SUR-ENG-ELE-01-04067 | 2022-04-26 | مطابق با مذاکرات انجام شده کلید بعد از تابلو دیزل ژنراتور (ورودی به سوییچگیر) به صورت NC در نظر گرفته شد. |  |  | Noted and Closed.
12 | No Comment. Note: According to our previous agreement, MPR shall be deleted and protection shall be shown base on different type of motor outgoing feeders and feeder type M4 shall be added. |  | BK-SUR-ENG-ELE-01-04478 | 2022-05-29 | مدرک بر اساس صورتجلسه در دفتر کارفرمای محترم و همچنین تغییرات مدرک LV Typical به روزرسانی گردید. و همچنین تیپ موتوری M4 اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: