## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | IN | DT | 0001 | D05
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR WHCP/HPU - WELLHEADS نگهداشت و افزایش تولید میدان نفتی بینک
D05 |  | MAR.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D04 |  | JAN.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D03 |  | JUN.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | DEC.2021 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | NOV.2021 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | AUG.2021 |  | IFC |  |  |  | M.Asgharnejad |  |  | M.Fakharian |  | Sh.Ghalikar
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F9Z-707368
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | IN | DT | 0001 |  | D05
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D05 |  | D06 |  | D07 | D08 | D09
1 | X | X | X |  | X |  | X |  | 1 |  | X
2 | X | X | X |  | X |  | X |  | 2 |  | X
3 | X | X | [6 empty] | 3
4 | X | X | [6 empty] | 4
5 | X | X | X | [5 empty] | 5
6 | X |  | X |  | X |  | X |  | 6 |  | X
7 | X |  | X |  |  |  | X |  | 7
8 | X |  | X |  | X |  | X |  | 8 |  | X
9 |  |  | X |  | X |  | X |  | 9
10 |  |  | X |  | X |  | X |  | 10
11 |  |  | X |  |  |  | X |  | 11
12 |  |  | X |  | X |  | X |  | 12
13 | [8 empty] | 13
14 | [8 empty] | 14
15 | [8 empty] | 15
16 | [8 empty] | 16
17 | [8 empty] | 17
18 | [8 empty] | 18
19 | [8 empty] | 19
20 | [8 empty] | 20
21 | [8 empty] | 21
22 | [8 empty] | 22
23 | [8 empty] | 23
24 | [8 empty] | 24
25 | [8 empty] | 25
26 | [8 empty] | 26
27 | [8 empty] | 27
28 | [8 empty] | 28
29 | [8 empty] | 29
30 | [8 empty] | 30
31 | [8 empty] | 31
32 | [8 empty] | 32
33 | [8 empty] | 33
34 | [8 empty] | 34
35 | [8 empty] | 35
36 | [8 empty] | 36
37 | [8 empty] | 37
38 | [8 empty] | 38
39 | [8 empty] | 39
40 | [8 empty] | 40
41 | [8 empty] | 41
42 | [8 empty] | 42
43 | [8 empty] | 43
44 | [8 empty] | 44
45 | [8 empty] | 45
46 | [8 empty] | 46
47 | [8 empty] | 47
48 | [8 empty] | 48
49 | [8 empty] | 49
50 | [8 empty] | 50
51 | [8 empty] | 51
52 | [8 empty] | 52
53 | [8 empty] | 53
54 | [8 empty] | 54
55 | [8 empty] | 55
56 | [8 empty] | 56
57 | [8 empty] | 57
58 | [8 empty] | 58
59 | [8 empty] | 59
60 | [8 empty] | 60
61 | [8 empty] | 61
62 | [8 empty] | 62
63 | [8 empty] | 63
64 | [8 empty] | 64

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0001 | D05
REFERENCE DOCUMENTS:
1- SPECIFICATION FOR INSTRUMENTATION | [10 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
2- PIPING AND PIPELINE MATERIAL SPECIFICATION | [10 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
3- PIPING & INSTRUMENT DIAGRAM:
|  | P&ID - W018S | [8 empty] | BK-W018S-PEDCO-110-PR-PI-0001
|  | P&ID - W028 | [8 empty] | BK-W028-PEDCO-110-PR-PI-0001
|  | P&ID - W035 | [8 empty] | BK-W035-PEDCO-110-PR-PI-0001
|  | P&ID - W008N | [8 empty] | BK-W008N-PEDCO-110-PR-PI-0001
4- SPECIFICATION FOR WHCP/HPU | [10 empty] | BK-SSGRL-PEDCO-110-IN-SP-0001
| 5- WHCP HYDRAULIC/PNEUMATIC DIAGRAM- WELLHEADS | [9 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
| 6- INSTRUMENT & CONTROL DESIGN CRITERIA | [9 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002

## Note 1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 12
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0001 | D05
GENERAL NOTES
1- Environmental Condition For Field Instrumentation Of Binak wellhead area Shall Be Considered
as Per The Following:
| • Minimum ambient temperature (°C): -5 °C • Maximum ambient temperature (°C): 50 °C • Maximum steel surface exposed to sun (°C): 85 °C | [9 empty] | 3 ºC
| Relative Humidity: | [9 empty] | 49 ºC
| • Maximum Design relative humidity: 100% • Minimum Design relative humidity: 0% | [9 empty] | 55 ºC
-5 ºC
46.5 ºC
100%@25.6 OC
2% @49.6 OC
13%

## 018S
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D05
WELLHEAD CONTROL PANEL FOR WELL NO. W018S
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1101
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W018S-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 100
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 75
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 6000 CC/2500 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 250 CC/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME(SECOND) | [7 empty] | 270 & 14-38/5-10 & 2-5 (NOTE 5)
|  |  | 14 | SSV ACTUATOR HYDRULIC DESIGN PRESSURE/SSSV ACTUATOR HYDRULIC DESIGN PRESSURE | [7 empty] | 5000 PSI
|  |  | 15 | SSV MAXIMUM WORKING PRESSURE/SSSV MAXIMUM WORKING PRESSURE | [7 empty] | 2500 PSI/3500 PSI (NOTE 5)
|  |  | 16 | SSV MINIMUM WORKING PRESSURE | [7 empty] | 600 PSI (NOTE 5)
|  |  | 17 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 18 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 19 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 20 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 21 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 22 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 23 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9,10)
|  |  | 24 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 25 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 26 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 27 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 28 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 29 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 30 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 31 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 33 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 34 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 35 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 36 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 37 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 38 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 39 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 40 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 41 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 42 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 43 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 44 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 45 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 46 | MANUFACTURER | [7 empty] | KARDANAN SHARGH CO.
|  |  | 47 | MODEL | [7 empty] | 400211 (KS Serial No.)
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1101A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1101A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 194.575
TAG NO. | PSHH-1101B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 242 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1101B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 242 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
10- QUICK EXAUST VALVE FOR QUICK OPENING OF SSV TO BE CONSIDERED BY WHCP'S VENDOR.
11- RETURN LINE FROM SSSV TO REURN OIL TANK TO BE CONSIDERED BY WHCP'S VENDOR.
D05

## 008N
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D05
WELLHEAD CONTROL PANEL FOR WELL NO. W008N
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1601
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W008N-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 100
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 75
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 6000 CC/2500 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 250 CC/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME(SECOND) | [7 empty] | 270 & 14-38/5-10 & 2-5 (NOTE 5)
|  |  | 14 | SSV ACTUATOR HYDRULIC DESIGN PRESSURE/SSSV ACTUATOR HYDRULIC DESIGN PRESSURE | [7 empty] | 5000 PSI
|  |  | 15 | SSV MAXIMUM WORKING PRESSURE/SSSV MAXIMUM WORKING PRESSURE | [7 empty] | 2500 PSI/3500 PSI (NOTE 5)
|  |  | 16 | SSV MINIMUM WORKING PRESSURE | [7 empty] | 600 PSI (NOTE 5)
|  |  | 17 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 18 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 19 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 20 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 21 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 22 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 23 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9,10)
|  |  | 24 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 25 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 26 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 27 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 28 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 29 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 30 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 31 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 33 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 34 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 35 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 36 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 37 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 38 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 39 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 40 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 41 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 42 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 43 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 44 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 45 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 46 | MANUFACTURER | [7 empty] | KARDANAN SHARGH CO.
|  |  | 47 | MODEL | [7 empty] | 400214 (KS Serial No.)
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1601A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1601A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1601B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 230 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1601B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 230 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
10- QUICK EXAUST VALVE FOR QUICK OPENING OF SSV TO BE CONSIDERED BY WHCP'S VENDOR.
11- RETURN LINE FROM SSSV TO REURN OIL TANK TO BE CONSIDERED BY WHCP'S VENDOR.
D05

## 028
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D05
WELLHEAD CONTROL PANEL FOR WELL NO. W028
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1401
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W028-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 105
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 80
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 6000 CC/2500 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 19 CC/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME(SECOND) | [7 empty] | 270 & 14-38/5-10 & 2-5 (NOTE 5)
|  |  | 14 | SSV ACTUATOR HYDRULIC DESIGN PRESSURE/SSSV ACTUATOR HYDRULIC DESIGN PRESSURE | [7 empty] | 5000 PSI
|  |  | 15 | SSV MAXIMUM WORKING PRESSURE/SSSV MAXIMUM WORKING PRESSURE | [7 empty] | 2500 PSI/3500 PSI (NOTE 5)
|  |  | 16 | SSV MINIMUM WORKING PRESSURE | [7 empty] | 600 PSI (NOTE 5)
|  |  | 17 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 18 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 19 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 20 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 21 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 22 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 23 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9,10)
|  |  | 24 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 25 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 26 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 27 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 28 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 29 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 30 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 31 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 33 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 34 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 35 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 36 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 37 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 38 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 39 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 40 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 41 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 42 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 43 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 44 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 45 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 46 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 47 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1401A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1401A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1401B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 273 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1401B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 273 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
10- QUICK EXAUST VALVE FOR QUICK OPENING OF SSV TO BE CONSIDERED BY WHCP'S VENDOR.
11- RETURN LINE FROM SSSV TO REURN OIL TANK TO BE CONSIDERED BY WHCP'S VENDOR.

## 035
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D05
WELLHEAD CONTROL PANEL FOR WELL NO. W035
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1501
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W035-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 105
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 80
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 6000 CC/2500 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 19 CC/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME(SECOND) | [7 empty] | 270 & 14-38/5-10 & 2-5 (NOTE 5)
|  |  | 14 | SSV ACTUATOR HYDRULIC DESIGN PRESSURE/SSSV ACTUATOR HYDRULIC DESIGN PRESSURE | [7 empty] | 5000 PSI
|  |  | 15 | SSV MAXIMUM WORKING PRESSURE/SSSV MAXIMUM WORKING PRESSURE | [7 empty] | 2500 PSI/3500 PSI (NOTE 5)
|  |  | 16 | SSV MINIMUM WORKING PRESSURE | [7 empty] | 600 PSI (NOTE 5)
|  |  | 14 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 15 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 16 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 17 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 18 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 19 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 20 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9,10)
|  |  | 21 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 22 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 23 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 24 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 25 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 26 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 27 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 28 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 29 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 30 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 31 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 33 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 34 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 35 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 36 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 37 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 38 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 39 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 40 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 41 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 42 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 43 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 44 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1501A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 1200
TAG NO. | PSLL-1501A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
TAG NO. | PSHH-1501B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 298 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 800
TAG NO. | PSLL-1501B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 298 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 200
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
10- QUICK EXAUST VALVE FOR QUICK OPENING OF SSV TO BE CONSIDERED BY WHCP'S VENDOR.
11- RETURN LINE FROM SSSV TO REURN OIL TANK TO BE CONSIDERED BY WHCP'S VENDOR.