## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0003-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1374 |  |  | Transmital Date: 07-Sep-2022
Document Title: DC Charger Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-1374 |  |  | Transmital Date: 07-Sep-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-SL-0003-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سطح مقطع کابل اتصال بدنه دستگاههای شارژر مطابق نقشه تک خطی ارسالی با نامه شماره 352430 مورخ 1400-10-16 به 70 میلی متر مربع افزایش یابد. |  | 1401-2294-238252 | 1401-07-05 | اعمال گردید.
2 | در صورتیکه در پیشنهاد فنی دریافتی از سازندگان سیستم F&G باتری و باتری شارژر (بر اساس نیازمندی پروژه) لحاظ شده باشد و باتری ها و دستگاههای شارژر همراه با فایر آلارم به تأیید کارفرما برسد، مقتضی است این مدرک و مدارک مرتبط حذف گردند. |  | 1401-2294-238252 | 1401-07-05 | مطابق با شرح کار پروژه و همچنین صورتجلسه مورخ 25-08-1401 در دفتر آن کارفرمای محترم مقرر گردید که یک دستگاه DC UPS صنعتی با ولتاژ 24 در نظر گرفته شود. از اینرو حذف باتری و تبدیل آن به باتری های تجاری در شرح کار پروژه نیست.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 21-Sep-22 |  |  |  |  | Date: