## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ST-DW-0045 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-1787 |  |  | Transmital Date:1/14/2023
Document Title: FOUNDATION DRAWING FOR COMPRESSOR AREA SECONDARY SLEEPERS |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0073-ST-TR-1787 |  |  | Transmital Date:1/14/2023
[5 empty] | CRS No:PEDCO-CRS- BK-GCS-PEDCO-120-ST-DW-0045_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | 1401/2294/443936 | 1401/11/19 | مدارک مرجع به نقشه ها اضافه گردید
2 |  |  | 1401/2294/443936 | 1401/11/19 | عایق لحاظ گردید
3 |  |  | 1401/2294/443936 | 1401/11/19 | اصلاح گردید
4 |  |  | 1401/2294/443936 | 1401/11/19 | اعمال گردید.
5 |  |  | 1401/2294/443936 | 1401/11/19 | لیست فوق تکمیل گردید
6 |  |  | 1401/2294/443936 | 1401/11/19 | مجددا با بخش سیویل کنترل گردید
7 |  |  | 1401/2294/443936 | 1401/11/19 | تراکم 95 درصد اضافه گردید
8 |  |  | 1401/2294/443936 | 1401/11/19 | شیب مجاز خاکبرداری طبق گزارش ژئوتکنیک 80 درجه می باشد که در مقاطع لحاظ گردید
9 |  |  | 1401/2294/443936 | 1401/11/19 | بکفیل با خاک مناسب مطابق استاندار و اسپک (Specification For Earth Work-(BK-GNRAL-PEDCO-000-CV-SP-0004 و کامپکشن بر همان اساس انجام میگیرد و تهیه قلوه در منطقه امکان پذیر نمی باشد.
10 |  |  | 1401/2294/443936 | 1401/11/19 | سنجاق های پیش بینی شده جهت اجرای میلگرد گذاری دیوار می باشد و در پای دیوار خاموت گذاری نیاز نمی باشد
11 |  |  | 1401/2294/443936 | 1401/11/19 | فواصل سنجاق ها اصلاح گردید
12 |  |  | 1401/2294/443936 | 1401/11/19 | پلان پی کنی اضافه شد
13 |  |  | 1401/2294/443936 | 1401/11/19 | عرض بتن مگر مشخص گردید و در مقاطع بتن مگر معرفی شده است
14 |  |  | 1401/2294/443936 | 1401/11/19 | در پلان میلگرد گذاری خطوط معرف بتن مگر حذف گردید
15 |  |  | 1401/2294/443936 | 1401/11/19
16 |  |  | 1401/2294/443936 | 1401/11/19 | بدلیل اتصال ورق روی پدستال با نبشی دوطرف گوشه دیوار امکان استفاده از گروت در زیر ورق نمی باشد
17 |  |  | 1401/2294/443936 | 1401/11/19 | مقاومت بتن اصلاح گردید
18 |  |  | 1401/2294/443936 | 1401/11/19 | اصلاح گردید
19 |  |  | 1401/2294/443936 | 1401/11/19 | نقطه نظرات اعمال گردید
20 |  |  | 1401/2294/466553 | 1401/12/07 | اعمال گردید.
21 |  |  | 1401/2294/466553 | 1401/12/07 | احتراما مد نظر قرار خواهد گرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: