## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | ME | DT | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | MAR. 2023 |  | AFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | JUN. 2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR. 2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-707351
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | ME | DT | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 | X |  | X | [5 empty] | 74
11 | X | X | X |  | X |  |  |  | 75
12 | X | X | [6 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Note 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  | BK | SSGRL | PEDCO | 110 | ME | DT | 0001 | D03
General Notes
Rev
| 1. | The Asterisk * denotes information and/or confirmation required from VENDOR. The Vendor shall be fully responsible for the complete
mechanical design and supply of the vessel. The vessel shall be supplied in accordance with BS EN 12285-2.
| 2. | Anchor bolts shall be calculated and sized by vendor.
| 3. | VENDOR shall include for the services of an independent verification body for mechanical design, stage inspection, testing and
stamping of the equipment (if possible).
| 4. | Specified accessories and attachments shall be supplied by vendor.
| 5. | Painting and coating (internal & external) shall be as per project 'Specification for Painting', Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006 and
Specification for Lining (Internal Protection of Equipment by painting), Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0007.
| 6. | Flanges shall comply with ANSI B16.5. Nozzle bolt holes shall stradle the natural centerlines. VENDOR to confirm maximum allowable nozzle
loads and moments. RF: Raised Face, WN: Welding Neck, SO: Slip On
| 7. | Equipment packaging, preparation for shipment and delivery shal be in accordance with the project minimum requirements for"Packing,
Marking, Transportation Procedure (Doc. No. BK-GNRAL-PEDCO-000-QC-PR-0045)."
| 8. | Manways shall be supplied complete with blind flange, external grab handles, internal grab handle and ladder rungs, nuts, bolting, gasket and
proof load test davits.
| 9. | Loads at support base, Shall be calculated and determined by vendor.
| 10. | The projection of equipment's nozzles should be as per 'Standard Detail Drawing For Pressure Vessels and Heat Exchangers', Doc. No.
BK-GNRAL-PEDCO-000-ME-DW-0001. (may be changed in furure).
Projection of Horizontal & Vertical nozzles is from tangent line & center line respectively.
| 11. | All external bolts and nuts shall be hot dip galvanized. Internal bolts and nuts shall be stainless steel.
| 12. | All dimensions shown are in mm unless otherwise indicated. All nozzle sizes are in inch.
| 13. | The vendor shall be responsible for mechanical strength of the equipment based on mentioned condition in data sheets.
| 14. | Dished ends shall be in accordance with BS EN 12285-2.
| 15. | Suitable Magnetic level gauge ( side mounted 2’’ 150# ) to be provided by vendor.
| 16. | All nozzles must be vertical or horizontal and not perpendicular or parallel to vessel center line.
| 17. | For standard detail of Earth lug execution refer to the Project "Standard Detail Drawing For Pressure Vessels and Heat Exchangers
Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001". Min two number shall be considered.
| 18. | Vendor shall supply details of all welding connections and give general specification of used materials.
| 19. | All materials shall be new and unused.
| 20. | Prior to sealing the vessel for shipping and storage, the inside surface of the equipment shall be 100% visually inspected. Internal surfaces shall
be clean and thoroughly dried. The CLIENT or its nominated representative shall witness the cleanliness of internal suarfaces. Hange faces shall
be protected by wooden or plastic dummy flanges.
| 21. | Fabrication tolerances for vessel shall be in accordance with requirement of BS EN 12285-2 code.
| 22. | All items shall be clearly match marked against vessel drawings to facilitate erection.
| 23. | The elevation of equipment's nozzels should be specified as follows :
I. For vertical vessels : from bottom T.L.
II. For horizontal vessels : from Left T.L.
| 24. | Gasket shall be spiral wound type, graphite filled with inner and outer rings S.S.316.
| 25. | The Vendor shall be fully responsible for the complete mechanical design, preparing calculation book and supply of the vessel.
| 26. | Hydrotest shall be carried out according to BS12285-2.
| 27. | Storage volume is for 36 hours, please refer to the project 'Consumption List' Doc. No. BK-SSGRL-PEDCO-110-PR-LI-0001".

## V-1901
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 4 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Diesel Oil Storage Drum of "BK-05" Well Pad (V-1901)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-1901 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (Sample P&ID) | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0003 / BK-W046S-PEDCO-110-PR-PI-0002
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes; Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## V-2001
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 5 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Diesel Oil Storage Drum "BK-12" Well Pad (V-2001)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-2001 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (Sample P&ID) | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0003 / BK-W046S-PEDCO-110-PR-PI-0002
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes;Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## V-2101
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 6 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Diesel Oil Storage Drum of "BK-14" Well Pad (V-2101)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-2101 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (Sample P&ID) | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0003 / BK-W046S-PEDCO-110-PR-PI-0002
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes;Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## V-2201
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 7 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Diesel Oil Storage Drum of "BK-15" Well Pad (V-2201)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-2201 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (Sample P&ID) | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0003 / BK-W046S-PEDCO-110-PR-PI-0002
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes;Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## V-1201
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 8 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Diesel Oil Storage Drum of "W007S" Well Pad (V-1201)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-1201 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (P&ID) | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0003
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes;Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## V-1301
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 9 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  |  | D03
Mech. Data Sheet for Fuel Oil Storage Drum of "W046S" Well Pad (V-1301)
Rev | DATA SHEET | [19 empty] | Rev
| 1 | Description | : |  | Fuel Oil Storage Drum
| 2 | Tag No. | : |  | V-1301 | [6 empty] | Quantity |  |  | : | 1 |  | Set
| 3 | Type | : |  | Storage Drum
| 4 | Process Design Data
| 5 | Contents |  |  |  | Diesel | [5 empty] | Corrosive / Erosive
| 6 | Operating Temp. |  |  | (oC) | Amb. | [5 empty] | Liquid Flow |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | Atm | [5 empty] | Vap. Molec. Weight |  |  |  | (kg/kmol) |  |  |  | N/A
| 8 | Gas Flow | (kg/h) |  |  | N/A | [5 empty] | Liquid Sp. Gravity | [7 empty] | 0.67~1
| 9 | Liquid Density |  | (kg/m3) |  | 860 | [5 empty] | Service: | [7 empty] | N/A
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [5 empty] | Vessel Orientation | [7 empty] | Horizontal
| 12 | Design Press. | (bar) |  |  | Full of water + Atm | [5 empty] | High Liquid Level (HLL) | [5 empty] | (mm) |  | 1050
| 13 | Test Press. | (barg) |  |  | 0.75 Liquid or 0.3 Air (Note 26) | [5 empty] | Nominal Liquid Capacity. | [6 empty] | (m3) | 4.2 (Note 27)
| 14 | Internal Vacuum |  | (barg) |  | - | [5 empty] | In. Dia. Of Boots |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 1250 | [5 empty] | Boot Length |  |  |  | (mm) |  |  |  | N/A
| 16 | Tan/Tan Dim. | (mm) |  |  | 3000 | [5 empty] | Boot Head Type | [7 empty] | N/A
| 17 | Vessel Head Type |  |  |  | Per Code & Specification (Note 14) | [5 empty] | Corr. Allowance |  |  |  | (mm) |  |  |  | 1.6
| 18 | Shell Wall Thk. | (mm) |  |  | 6* | [5 empty] | Joint Efficiency | [7 empty] | 0.7
| 19 | Head Wall Thk. | (mm) |  |  | 6* | [5 empty] | Ambient Temp. |  |  |  | (oC)
| 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [5 empty] | MDMT |  |  |  | (oC) |  |  |  | -5
| 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [5 empty] | Insulation Required | [7 empty] | No
| 22 | Materials
| 23 | Code |  |  |  |  | ASTM |  |  |  |  | Nozzle Necks:
| 24 | Shell |  |  |  |  | A 285 Gr.C |  |  |  |  | Pipes | [7 empty] | A 106 Gr.B
| 25 | Heads |  |  |  |  | A 285 Gr.C |  |  |  |  | Plates | [7 empty] | A 285 Gr. C
| 26 | Lining / Cladding |  |  |  |  | P8 |  |  |  |  | Forgings | [7 empty] | A 105
| 27 | Saddle |  |  |  |  | A 285 Gr. C |  |  |  |  | Flanges | [7 empty] | A 105
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. |  |  |  |  | Fittings | [7 empty] | A 234 Gr. WPB
| 29 | Gaskets |  |  |  |  | Note 26 |  |  |  |  | External Bolts | [7 empty] | A 193 Gr. B7 (Note 11)
| 30 | Lifting Lugs |  |  |  |  | A 285 Gr. C |  |  |  |  | External Nuts | [7 empty] | A 194 Gr. 2H (Note 11)
| 31 | Reinforcing Pads |  |  |  |  | A 285 Gr.C |  |  |  |  | Internal Bolts / Nuts | [7 empty] | S.S.
| 32 | Ladder & Platform |  |  |  |  | A 36 |  |  |  |  | Name Plate | [7 empty] | S.S. 316
33
| 34 | REFERENCE STANDARDS & DOCUMENTS
| 35 | Mechanical Design Code | [9 empty] | BS EN 12285-2
| 36 | Process Basis of Design | [9 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 37 | Piping & Instrument Diagram (P&ID) | [9 empty] | BK-W046S-PEDCO-110-PR-PI-0002
| 38 | Specification for Painting | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 39 | Specification for Insulation | [9 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 40 | Consumption List | [9 empty] | BK-SSGRL-PEDCO-110-PR-LI-0001
41
| 42 | Fabrication and Inspection Requirements
| 43 | Inspection Authority |  |  |  |  | TPI & Client
| 44 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1
| 45 | Hydro Test Medium |  |  |  |  | Water |  |  |  |  | Hydro Test Procedure | [6 empty] | Yes;Per BS EN 12285-2 Standard
| 46 | MT |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT | [6 empty] | Yes;Per Code & Spec. Requirements
| 47 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. |  |  |  |  | PT Report | [6 empty] | Yes;Per Code & Spec. Requirements
| 48 | Fabrication Quality Control Plan (With Offer) | [9 empty] | Yes
| 49 | Welding Procedure Review / Approval | [9 empty] | Yes
| 50 | Surface Preparation & Coating | [9 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006" Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
51
52
53
54
55
56
57
58
59
60
61
62

## Sheet 1
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 10 از 12
9184 – 073 - 053 | [6 empty] | BK |  | SSGRL | PEDCO | 110 | ME |  | DT | 0001 |  | D03
Data Sheets for Fuel Oil Storage Drum of Well Pads
Rev. | ACCESSORIES , NOZZLES LIST & LOADS @ BASE | [21 empty] | Rev.
| 1 | Accessories & Attachments (Note 4)
| 2 | Supporting Saddles | [8 empty] | Yes |  | Name Plate Bracket | [8 empty] | Yes
| 3 | Access Ladder & Platform | [8 empty] | Yes |  | Name Plate | [8 empty] | Yes
| 4 | Insulation Support | [8 empty] | No |  | Earthing Lug (Note 17) | [8 empty] | Yes
| 5 | Insulation | [8 empty] | No |  | Tailing Lug | [8 empty] | Yes
| 6 | Insulation Cover | [8 empty] | No |  | Cathodic Protection (Sacrificial Anodes) | [8 empty] | No
| 7 | Fireproofing Support | [8 empty] | No |  | Anchor Bolts (Note 2) | [8 empty] | No
| 8 | Lifting Lugs | [8 empty] | Yes |  | Instrumentations | [8 empty] | Yes
| 9 | Internal/ External Clips | [8 empty] | Yes |  | Skid | [8 empty] | No
| 10 | Template | [8 empty] | No |  | Support Clips | [8 empty] | Yes
| 11 | Boot | [8 empty] | No |  | Vortex Breaker | [8 empty] | No
| 12 | Davit for Manhole | [8 empty] | Yes |  | Rung & Grip | [8 empty] | No
| 13 | Internal Lining (By Painting) | [8 empty] | Yes |  | Heating Coil | [8 empty] | No
14
15
16
17
| 18 | Nozzles List * (Note 1, 6, 10)
| 19 | Mark |  | Qty. |  | Description |  |  |  | Pipe |  |  |  | Flange |  |  |  | Proj. | (mm) | Reinforcement |  | Remarks
| 20 | [8 empty] | Size | Thk. | Sch. |  | Type | Rate. | Face |  | (Note 10) |  | Thk. | O.D.
D03 | 21 |  | A | 1 |  | Inlet |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 781*
D03 | 22 |  | B | 1 |  | Outlet |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 781*
D03 | 23 |  | V | 1 |  | Vent |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 781*
D03 | 24 |  | D | 1 |  | Drain |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 781*
D03 | 25 |  | L 1,2 | 2 |  | Level Gauge |  |  |  | 2" |  |  |  | WN | #150 | RF |  | 781* |  |  |  | Note 15
D03 | 26 |  | M | 1 |  | Manway |  |  |  | 24" |  |  |  | WN | #150 | RF |  | 937* |  | 6* | 1050*
27
28
29
30
31
32
33
| 34 | Wind and Seismic Loads at Base * Note (9)
| 35 |  | Load Condition |  | Empty Condition | [5 empty] | Operating Condition | [5 empty] | Testing Condition
36
| 37 |  |  |  | Max. Shear @ Base (Kg) |  |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) |  | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg)
38
| 39 |  | Load Type
40
41
| 42 | WIND
43
| 44 | SEISMIC
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62

## Sheet 2
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 12
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 110 | ME | DT | 0001 | D03
Data Sheets for Fuel Oil Storage Drum of Well Pads
Sketch
All dimensions are in mm.

## Sheet 3
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 12 از 12
9184 – 073 - 053 | [6 empty] | BK | SSGRL |  | PEDCO |  | 110 | ME |  | DT | 0001 |  | D03
Data Sheets for Fuel Oil Storage Drum of Well Pads
Rev. | WEIGHT | [21 empty] | Rev.
| 1 | WEIGHT CONTROL DATA SHEET SI UNIT * | [12 empty] | 1/1
2
3
4
5
| 6 | Service |  | : |  | Fuel Oil Storage Drum | [8 empty] | Location |  | : | Bushehr (Binak Oilfield)
| 7 | Type |  | : | [10 empty] | Quotation No. |  | :
| 8 | No. trains |  | : | [10 empty] | Serial No. |  | :
| 9 | No. stages |  | :
| 10 | Supplier |  | :
| 11 | Manufacturer |  | :
| 12 | Model |  | :
13
| 14 | Note: Information to be completed by equipment vendor.
15
| 16 | Total weight (kg) *
| 17 | Fabrication |  |  | Erection |  |  |  | Operation |  |  |  |  | Hydrostatic Test |  |  |  | Removable internal |  |  | Ladder & Platform
18
19
20
21
22
| 23 | WEIGHT AND C OF G DATA REQUIRED *
| 24 | CONDITION |  |  |  | WEIGHT ACCURACY % |  |  |  |  | WEIGHT (kg) |  |  |  |  | CENTER OF GRAVITY (mm)
| 25 | [14 empty] | X |  |  | Y |  |  | Z
| 26 | Dry
27
28
29
| 30 | SKETCH
31
32
33
| 34 | [13 empty] | ASME BPVC VIII, DIV.1
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
| 52 | NOTES
| 53 | 1) | All lifting points to be load tested and certified.
| 54 | 2) | Any spreader beam to be load tested and certified.
| 55 | 3) | Lifting / rigging plan for skid mounted equipment to be provided by the Vendor.
56
57
58
59
60
61