## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | LI | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT INDEX نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | MAR.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | FEB.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708608
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | LI | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | X |  | X |  |  |  | 67
4 | X | X | X | [5 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTES
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 4
9184 – 073 - 053 |  |  |  |  | BK | PPL | PEDCO | 320 | IN | LI | 0001 | D03
REFERENCES:
| P&ID - GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | [9 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D02
| P&ID - CONDENSATE PIPELINE (TO BINAK PU) | [9 empty] | BK-PPL-PEDCO-320-PR-PI-0002_D02
| P&ID - SYMBOL & LEGEND for PFD and P&ID | [9 empty] | BK-PPL-PEDCO-320-PR-PI-0003_D01
ABBREVIATIONS:
|  | CC |  | CORROSION COUPON
|  | CP/T |  | CORROSION PROBE/ TRANSMITTER
|  | PSHH/PSLL |  | PRESSURE SWITCH HIGH HIGH/LOW LOW LEVEL SHUTDOWN
|  | PRV/PSV |  | PRESSURE RILIEF/SAFTEY VALVE
|  | PT |  | PRESSURE TRANSMITTER
|  | PCV |  | PRESSURE CONTROL VALVE
|  | PG |  | PRESSURE GAUGE
|  | TRV |  | TEMPERATURE RILIEF VALVE
|  | TG |  | TEMPERATURE GAUGE
|  | TT |  | TEMPERATURE TRANSMITTER
|  | XV |  | ON/OFF VALVE
|  | ESDV |  | EMERGENCY SHUTDOWN VALVE
|  | BDV |  | BLOWDOWN VALVE
|  | FE |  | FLOW ELEMENT
|  | FT |  | FLOW TRANSMITTER
|  | FCV |  | FLOW CONTROL VALVE
|  | ZI |  | PIG SIGNALER INDICATOR
|  | ZS |  | PIG SIGNALER SWITCH
|  | DS |  | DOOR OPEN SWITCH
|  | TDS |  | TOTAL DISSOLVED SOLID
|  | IS |  | INTRINSICALLY SAFE
|  | NIS |  | NON INTRINSICALLY SAFE
|  | R |  | REDUNDANT
|  | NR |  | NON REDUNDANT
|  | IO |  | INPUT / OUTPUT
|  | DI |  | DIGITAL INPUT SIGNAL
|  | DO |  | DIGITAL OUTPUT SIGNAL
|  | AI |  | ANALOGUE INPUT SIGNAL
|  | AO |  | ANALOGUE OUTPUT SIGNAL
|  | DCS |  | DISTRIBUTED CONTROL SYSTEM
|  | ESD |  | EMERGENCY SHUT DOWN SYSTEM
NOTES:
| NOTE 1: |  | Over Pressure Protection Shall Be Provided For The Device Considering Design Pressure.
| NOTE 2: |  | HART COMMUNICATOR DEVICE" provided in GCS work pack will be used for Calibrating of the transmitters.
| NOTE 3: |  | Rotameter process data will be finilized after receiving the data from client.
| NOTE 4: |  | The ESDV -3202 will be provided as new and shall Be Connected To new devices added to Siahmakan Existing Control & Emergency Shutdown Systems as extention.
| NOTE 5: |  | This Rotameter to be considered in datasheet 'BK-GCS-PEDCO-120-IN-DT-0018' and to be supplied with
Binak GCS Rotameters.
D03

## Instrument Index
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
INSTRUMENT INDEX
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | [5 empty] | شماره صفحه: 4 از 4
9184 – 073 - 053 |  |  |  |  | BK | PPL | PEDCO | 320 |  | IN | LI | 0001 | D03
IDENTIFICATION |  |  | REFERENCE | [9 empty] | PRESSURE (Barg) |  | TEMPERATURE (°C) |  | INSTRUMENT RANGE | CALIBRATION RANGE | INSTRUMENT UNIT | SYSTEM CONTROL | I/O TYPE | SIGNAL TYPE | REMARK | REV.
ITEM | TAG | DESCRIPTION | LINE/ EQUIPMENT | P&ID |  | SERVICE | LOCATION/ PACKAGE NAME | DATA SHEET NO. | HOOK UP DWG. NO. |  | LOOP DWG NO. | LOCAION LAYOUT DWG NO. | DESIGN Barg | OPER. Barg | DESIGN | OPER. °C
1 | ESDV-3201 | Emergency Shutdown Valve (Body) | GAS-111-0072-FN05-6"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | - | - | -
2 | EZSC-3201 | Limit Switch Close | GAS-111-0072-FN05-6"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | ESD (of new GCS) | DI-NIS-R | 24 VDC
3 | EZSO-3201 | Limit Switch Open | GAS-111-0072-FN05-6"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | ESD (of new GCS) | DI-NIS-R | 24 VDC
4 | PSOV-3201 | Solenoid Valve | GAS-111-0072-FN05-6"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0005 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | DCS (of new GCS) | DO-NIS-NR | 24VDC LOOP POWER
5 | ESOV-3201 | ESD Solenoid Valve | GAS-111-0072-FN05-6"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | ESD (of new GCS) | DO-NIS-R | 24VDC LOOP POWER
6 | PT-3201A | PRESSURE TRANSMITTER | GAS-113-0072-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0003 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 |  |  | Barg | ESD (of new GCS) | AI-IS-R | 4-20 mA | Note 2
7 | PT-3201B | PRESSURE TRANSMITTER | GAS-113-0072-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0003 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 |  |  | Barg | ESD (of new GCS) | AI-IS-R | 4-20 mA | Note 2
8 | PT-3201C | PRESSURE TRANSMITTER | GAS-113-0072-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0003 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 |  |  | Barg | ESD (of new GCS) | AI-IS-R | 4-20 mA | Note 2
9 | PG-3201 | PRESSURE GAUGE | PL-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) PIG LAUNCHER | BK-PPL-PEDCO-320-IN-DT-0001 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 |  |  | Barg | - | - | - | NOTE 1
10 | PSV-3201 | PRESSURE SAFETY VALVE | GAS-113-0003-FN05-2"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) PIG LAUNCHER | BK-PPL-PEDCO-320-IN-DT-0005 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | - | - | -
11 | FG-3201 | FLOW GAUGE ROTAMETER | CHM-112-0007-FS00-3/4"-NP | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | FROM METHANOL HEADER (TO SIAHMAKAN G.I. STATION) | BK-GCS-PEDCO-120-IN-DT-0018 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | NOTE 3 | NOTE 3 | NOTE 3 | NOTE 3 | - | - |  | - | - | - | NOTE 5
12 | PG-3202 | PRESSURE GAUGE | GAS-113-0005-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) AFTER PIG LAUNCHER | BK-PPL-PEDCO-320-IN-DT-0001 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | Barg | - | - | - | -
13 | ZI-3201 | PIG INDICATOR | GAS-113-0005-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) AFTER PIG LAUNCHER | BK-PPL-PEDCO-320-IN-DT-0010 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 50.9 | 85 | 58.3 | - | - | - | - | - | - | - | -
14 | LBV-3201 | LINE BREAK VALVE | GAS-113-0007-FN27-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (2/3) |  | GAS | AFTER PIG LAUNCHER, NEAR THE BEGINNING OF PIPELINE | BK-PPL-PEDCO-320-IN-DT-0012 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 43.9 | 85 | 31.78 | - | - | - | - | - | -
15 | LBV-3202 | LINE BREAK VALVE | GAS-113-0009-FN27-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (2/3) |  | GAS | BEFOR PIG RECEIVER, NEAR THE END OF PIPELINE | BK-PPL-PEDCO-320-IN-DT-0012 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 43.9 | 85 | 31.78 | - | - | - | - | - | -
16 | CC-3202 | CORROSION COUPON | CDH-113-0004-AN07-2"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) BEFOR PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0009 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 |  |  | - | - | - | -
17 | PG-3203 | PRESSURE GAUGE | GAS-113-0011-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) BEFOR PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0001 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 |  |  | Barg | - | - | - | -
18 | TG-3202 | TEMPERATURE GAUGE | GAS-113-0015-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) BEFOR PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0002 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 |  |  | °C | - | - | -
19 | ZI-3202 | PIG INDICATOR | PR-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) BEFOR PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0010 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | - | - | - | -
20 | PG-3204 | PRESSURE GAUGE | PR-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) BEFOR PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0001 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 |  |  | Barg | - | - | - | -
21 | ZI-3203 | PIG INDICATOR | PR-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0010 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | - | - | - | -
22 | PG-3205 | PRESSURE GAUGE | PR-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0001 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 |  |  | Barg | - | - | - | -
23 | PSV-3202 | PRESSURE SAFETY VALVE | GAS-113-0014-FN05-2"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) PIG RECEIVER | BK-PPL-PEDCO-320-IN-DT-0005 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | - | - | -
24 | ESDV-3202 | Emergency Shutdown Valve (Body) | GAS-113-0115-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | - | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | - | - | -
25 | EZSC-3202 | Limit Switch Close | GAS-113-0115-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | EXISTING ESD/DCS | DI-NIS-R | 24 VDC | NOTE 4
26 | EZSO-3202 | Limit Switch Open | GAS-113-0115-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | EXISTING ESD/DCS | DI-NIS-R | 24 VDC | NOTE 4
27 | PSOV-3202 | Solenoid Valve | GAS-113-0115-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0005 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | EXISTING ESD/DCS | DO-NIS-NR | 24VDC LOOP POWER | NOTE 4
28 | ESOV-3202 | ESD Solenoid Valve | GAS-113-0115-FN05-8"-PT | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  | GAS | GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | BK-PPL-PEDCO-320-IN-DT-0006 | BK-PPL-PEDCO-320-IN-DG-0002 |  | BK-PPL-PEDCO-320-IN-DG-0004 | BK-PPL-PEDCO-320-IN-PY-0002 | 62 | 40 | 85 | 31.3 | - | - | - | EXISTING ESD/DCS | DO-NIS-R | 24VDC LOOP POWER | NOTE 4