## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-PY-0005_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1835 |  |  | Transmital Date: 31 Jan 2023
Document Title: F&G Location Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1835 |  |  | Transmital Date: 31 Jan 2023
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-PY-0005_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-06945 | 2023-02-15 | ملاحظه گردید.
2 | در صفحه 4 مدرك در area شماره 18؛ (Battery room) سنسور smoke detector در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-06945 | 2023-02-15 | با توجه به استاندارد IPS- E-sf-260 استفاده از هر یک از انواع دتکتور Heat یا smoke مورد تایید میباشد.
3 | لزوم استفاده از آلارم ديداري قرمز در ضلع جنوب ساختمان كنترل بررسي گردد. |  | BK-SUR-ENG-INS-01-06945 | 2023-02-15 | با توجه به ابعاد کوچک اتاق کنترل و شعاع پوشش دهی چراغ های هشدار نیازی به در نظر گیری دو چراغ هشدار قرمز برای این اتاق نخواهد بود و با توجه به کامنت کارفرمای محترم بین ضلع جنوبی و شمالی ساختمان قرار داده شد.
4 | نقطه نظرات ذي نفع اصلي بر روي اين مدرك در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-06945 | 2023-02-15 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 14 Feb 2023 |  |  |  |  | Date: