## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | LI | 0004 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | MAR.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | AUG.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 1 |  |  |  | CLIENT Doc. Number: F0Z-708005
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for COMPANY Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0004 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | [7 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | [6 empty] | 69
6 |  | X | X | [5 empty] | 70
7 |  | X | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | LI |  | 0004 | D02
REFERENCES:
| F&G LOCATION LAYOUT - EXTENSION OF BINAK BC MANIFOLD | [7 empty] | BK-W007S-PEDCO-110-IN-PY-0005
ABBREVIATIONS:
| I/O | INPUT / OUTPUT | [5 empty] | DCS: |  | DISTRIBUTED CONTROL SYSTEM
| DI: | DIGITAL INPUT SIGNAL | [5 empty] | ESD: |  | EMERGENCY SHUT DOWN SYSTEM
| DO: | DIGITAL OUTPUT SIGNAL | [5 empty] | F&G |  | FIRE AND GAS CONTROL SYSTEM
| AI: | ANALOGUE INPUT SIGNAL | [5 empty] | MCC: |  | MOTOR CONTROL CENTER
| AO: | ANALOGUE OUTPUT SIGNAL | [5 empty] | IRP: |  | INTERPOSING RELAY PANEL
| IND: | INDICATION | [5 empty] | CH: |  | CHANNEL
| STA: | STATUS | [5 empty] | ADD: |  | ADDRESS
| COM: | COMMAND | [5 empty] | TB: |  | TERMINAL BLOCK
| IS: | INTRINSICALLY SAFE | [5 empty] | R: |  | REDUNDANT
| NIS: | NON INTRINSICALLY SAFE | [5 empty] | NR: |  | NON-REDUNDANT
| MAC: | MANUAL CALL POINT | [5 empty] | BR: |  | BLUE BEACON
| HN: | HORN | [5 empty] | BB: |  | RED BEACON
| LHD: | LINEAER HEAT DETECTOR | [5 empty] | FGD: |  | FLAMMABLE GAS DETECTOR
| SD: | SMOKE DETECTOR | [5 empty] | TGD: |  | TOXIC GAS DETECTOR
| BL: | BELL | [5 empty] | FD: |  | FLAME DETECTOR
| FACP: | FIRE ALARM CONTROL PANEL | [5 empty] | IRP: |  | INTERFACE RELAY PANEL
NOTE 1 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
NOTE 2 : |  | DETAIL INFORMATION OF SYSTEM CABINETS AND MARSHALLING CABINETS INCLUDING: CABINET NAME, RACK AND SLOT NUMBERS, NUMBER OF CHANNELS, ADDRESS OF I/O SIGNALS, TERMINAL BLOCK STRIP NAMES, WHICH ARE SHOWN WITH “*” NOW, WILL BE COMPLETED IN CONTROL SYSTEM VENDORS DOCUMENTS.

## SUMMARY
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0004 | D02
F&G I/O SUMMERY COUNT
| ITEM | I/O TYPE | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 | LOOP 1 | - | - |  | 21 IP | [6 empty] | - |  | - | Addressable
| 2 | LOOP 2 | - | - |  | 7 IP | [6 empty] | - |  | - |  | Addressable
| 3 | LOOP 3 | - | - |  | 1 No. Analog 4~20 mA loop | [6 empty] | - |  | - | Conventional
| 4 | LOOP 4 | - | - |  | 24 IP | [6 empty] | - |  | - |  | Addressable
| 5 | LOOP 5 | - | - |  | 1 No. Analog 4~20 mA loop | [6 empty] | - |  | - | Conventional
D02

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O List For F&G System - Extension of Binak B/C Manifold
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | LI | 0004 | D02
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION | P&ID | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | REMARK | REV.
[11 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
1 | FACP | Output Port of Loop1 | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | FACP | HN-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
2 | HN-2101 | Horn | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | HN-2101 | BR-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
3 | BR-2101 | Beacon | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BR-2101 | MAC-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
4 | MAC-2101 | Manual Call Point | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2101 | BR-2102 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
5 | BR-2102 | Beacon | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BR-2102 | BL-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
6 | BL-2101 | Bell | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BL-2101 | SD-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
7 | SD-2101 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2101 | SD-2122 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
8 | SD-2122 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2122 | SD-2114 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
9 | SD-2114 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2114 | SD-2113 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
10 | SD-2113 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2113 | SD-2102 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
11 | SD-2102 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2102 | SD-2121 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
12 | SD-2121 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2121 | MAC-2104 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
13 | MAC-2104 | Manual Call Point | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2104 | SD-2111 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
14 | SD-2111 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2111 | MAC-2103 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
15 | MAC-2103 | Manual Call Point | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2103 | SD-2103 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
16 | SD-2103 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2103 | HD-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
17 | HD-2101 | Heat Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | HD-2101 | SD-2105 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
18 | SD-2105 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2105 | SD-2112 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
19 | SD-2112 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2112 | SD-2106 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
20 | SD-2106 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2106 | SD-2104 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
21 | SD-2104 | Smoke Detector | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2104 | MAC-2102 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
22 | MAC-2102 | Manual Call Point | CONTROL BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2102 | FACP | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
23 | FACP | Output Port of Loop 2 | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | FACP | MAC-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
24 | MAC-2201 | Manual Call Point | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2201 | HD-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
25 | HD-2201 | Heat Detector | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone1, IIC T4 | Addressable | HD-2201 | HN-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
26 | HN-2201 | Horn | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | HN-2201 | BY-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
27 | BY-2201 | Beacon | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BY-2201 | BR-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
28 | BR-2201 | Beacon | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BR-2201 | SD-2201 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
29 | SD-2201 | Smoke Detector | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2201 | MAC-2202 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
30 | MAC-2202 | Manual Call Point | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2202 | FACP | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
31 | HGD-2201 | Hydrogen Gas Detector | BATTERY ROOM AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone1, IIC T4 | AI-NIS-NR | HGD-2201 | FACP | 4-20 mA | By Vendor | - | - | - | - | - | - | - | loop 3 | D02
32 | FACP | Output Port of Loop 4 | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | FACP | MAC-2302 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
33 | MAC-2302 | Manual Call Point | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2302 | HN-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
34 | HN-2301 | Horn | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | HN-2301 | BR-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
35 | BR-2301 | Beacon | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BR-2301 | BY-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
36 | BY-2301 | Beacon | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BY-2301 | SD-2303 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
37 | SD-2303 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2303 | SD-2316 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
38 | SD-2316 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2316 | SD-2315 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
39 | SD-2315 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2315 | HD-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
40 | HD-2301 | Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone1, IIC T4 | Addressable | HD-2301 | MAC-2303 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
41 | MAC-2303 | Manual Call Point | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2303 | LHD-2305 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
42 | LHD-2305 | Linear Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | LHD-2305 | LHD-2304 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
43 | LHD-2304 | Linear Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | LHD-2304 | SD-2313 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
44 | SD-2313 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2313 | MAC-2304 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
45 | MAC-2304 | Manual Call Point | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2304 | LHD-2303 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
46 | LHD-2303 | Linear Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | LHD-2303 | LHD-2302 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
47 | LHD-2302 | Linear Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | LHD-2302 | SD-2312 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
48 | SD-2312 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2312 | SD-2311 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
49 | SD-2311 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2311 | SD-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
50 | SD-2301 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2301 | LHD-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
51 | LHD-2301 | Linear Heat Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | LHD-2301 | SD-2314 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
52 | SD-2314 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2314 | SD-2302 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
53 | SD-2302 | Smoke Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2302 | BL-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
54 | BL-2301 | Bell | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BL-2301 | BR-2302 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
55 | BR-2302 | Beacon | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BR-2302 | MAC-2301 | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
56 | MAC-2301 | Manual Call Point | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2301 | FACP | 24 VDC | By Vendor | - | - | - | - | - | - | - |  | D02
57 | HGD-2301 | Hydrogen Gas Detector | SWITCH GEAR BUILDING AREA | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone1, IIC T4 | AI-NIS-NR | HGD-2301 | FACP | 4-20 mA | By Vendor | - | - | - | - | - | - | - | loop 5 | D02
D02