## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 21
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0010 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | APR.2023 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | JAN.2023 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | SEP.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 1 |  |  |  | Client Doc. Number: F9Z-707980
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 21
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0010 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | X | [6 empty] | 70
7 | X |  | X | [5 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | X | X | X | [5 empty] | 74
11 | X |  | X | [5 empty] | 75
12 | X | X | [6 empty] | 76
13 | X |  | X | [5 empty] | 77
14 | X | X | [6 empty] | 78
15 | X | [7 empty] | 79
16 | X | X | [6 empty] | 80
17 | X | X | [6 empty] | 81
18 | X | X | [6 empty] | 82
19 | X |  | X | [5 empty] | 83
20 | X | X | X | [5 empty] | 84
21 | X |  | X | [5 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0010 | D02
REFERENCE DOCUMENTS :
| F&G LOCATION LAYOUT - EXTENSION OF BINAK BC MANIFOLD | [6 empty] | BK-W007S-PEDCO-110-IN-PY-0005
| FIRE AND GAS DETECTION DESIGN CRITERIA | [6 empty] | BK-SSGRL-PEDCO-110-IN-DC-0001
| SPECIFICATION FOR FIRE & GAS SENSOR AND DEVICES | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0009
GENERAL NOTE
| 1 | Refer to latest version of reference documents.

## Note
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 21
9184 – 073 - 053 | BK | W007S | PEDCO | 110 | IN | DT | 0010 | D02
GENERAL NOTES:
1 - Vendor shall identify and detail any deviation from the present Data Sheet
2- All equipments/detectors listed in this document shall be supplied with related calibration and test equipments.
3 - S.S. Name olate including project description to be provided.

## CONTENTS
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 21
9184 – 073 - 053 |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
CONTENTS
| ITEMS | [9 empty] | PAGES
| DATASHEET FOR HORN |  |  |  | ………………………………………………………………………….. | [5 empty] | 6
| HORN LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 7
| DATASHEET FOR BEACON |  |  |  | ………………………………………………………………………….. | [5 empty] | 8
| BEACON LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 9
| DATASHEET FOR HYDROGEN GAS DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 10
| HYDROGEN GAS DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 11
| DATASHEET FOR MANUAL ALARM CALL POINT |  |  |  | ………………………………………………………………………….. | [5 empty] | 12
| MANUAL ALARM CALL POINT LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 13
| DATASHEET FOR LINEAR HEAT DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 14
| LINEAR HEAT DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 15
| DATASHEET FOR SMOKE DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 16
| SMOKE DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 17
| DATASHEET FOR BELL |  |  |  | ………………………………………………………………………….. | [5 empty] | 18
| BELL LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 19
| DATASHEET FOR HEAT DETECTOR |  |  |  | ………………………………………………………………………….. | [5 empty] | 20
| HEAT DETECTOR LIST |  |  |  | ………………………………………………………………………….. | [5 empty] | 21

## HORN
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN |  | DT | 0010 | D02
DATASHEET FOR HORN
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | Addressable
| 9 | Function | [5 empty] | Local Alarm with 2 modes: • non-continuous for flammable and toxic gas low alarm detection • Continuous for fire detection and also flammable/toxic gas high alarm detection
| 10 | Sound Pressure Level | [5 empty] | 120 dB (At 1 meter) (VTC)
| 11 | Service | [5 empty] | Hydrocarbon
| 12 | Adjustable Sound Intensity | [5 empty] | Yes
| 13 | Frequency Range | [5 empty] | 500 ~ 1000 Hz (VTC)
| 14 | Multiple Terminal Connection | [5 empty] | Required
| 15 | No. of Selectable Tones | [5 empty] | Minimum 2
| 16 | Power Supply | [5 empty] | 24 VDC
| 17 | System Wiring | [5 empty] | 10 Core x 1.5 (for Horn combined with Blue/ Red Beacon)(Note 9)
| 18 | Power Consumption | [5 empty] | VTA (Note 4)
| 19 | Electrical Connection | [5 empty] | M25 x 1.5(Note 9 )
| 20 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum (copper free).
| 21 | Installation | [5 empty] | Fix
| 22 | Mounting | [5 empty] | Bracket (Note 2)
| 23 | Mounting Accessories Material | [5 empty] | 316 SS
| 24 | Degree of Protection | [5 empty] | IP 65
| 25 | Explosion Protection | [5 empty] | Unclassified
| 26 | Weather Proof and Dust Proof | [5 empty] | Yes
| 27 | Safety Integrity Level | [5 empty] | Non SIL
| 28 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 29 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 30 | Manufacturer | [5 empty] | will be finalized later
| 31 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. The value of End Of Line (EOL) resistor shall be suggested by vendor. 4. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 5. 2 different tones one for Flammable/ Toxic gas detection (non-continuous) and one for fire detection (continuous). Each tone shall be activated by receiveing dedicated signal. 6. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Horn alarms shall have a range of at least 1.5 km in still air. 9. Horn and related beacon(Red) shall be installed on common stand. Eex JB for connectig 5*1.5 mm2 cable to be considered by vendor for signal distribution.

## HORN list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 7 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
HORN LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | HN-2101 (Note 9 at page 6) | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
2 | HN-2201(Note 9 at page 6) | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
3 | HN-2301(Note 9 at page 6) | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
9
10
11
12
13 | Calibration and test device for Horn | [12 empty] | NOTE 1
1. Calibration and test devices for Horn to be advise by vendor.
D02

## BB-BR
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR BEACON
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | Addressable
| 9 | Service | [5 empty] | See Next Page
| 10 | Function | [5 empty] | • Red for fire detection • Yellow for flammable gas detection • Blue for Toxic Gas Detector(if applicable)
| 11 | Flash Rate | [5 empty] | 60 FPM/1HZ (VTA)
| 12 | Colour | [5 empty] | See Next Page
| 13 | Lens Type | [5 empty] | Glass
| 14 | Field of View | [5 empty] | 360°
| 15 | Tube type | [5 empty] | Xenon
| 16 | Effective Intensity | [5 empty] | 200 cd to 1000 cd candela (VTA)
| 17 | Power Supply | [5 empty] | 24 VDC (VTA)
| 18 | System Wiring | [5 empty] | 10 Core x 1.5 (for Horn combined with Blue/ Red Beacon) (Note 8)
| 19 | Power Consumption | [5 empty] | VTA (Note 4)
| 20 | Electrical Connection | [5 empty] | M20 x 1.5
| 21 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 22 | Installation | [5 empty] | Fix
| 23 | Mounting | [5 empty] | Bracket (Note 2)
| 24 | Mounting Accessories Material | [5 empty] | 316 SS
| 25 | Degree of Protection | [5 empty] | See Next Page
| 26 | Explosion Protection | [5 empty] | See Next Page
| 27 | Weather Proof and Dust Proof | [5 empty] | Yes
| 28 | Safety Integrity Level | [5 empty] | Non SIL
| 29 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 30 | Body Color | [5 empty] | • Red for fire and flammable gas detection • Red for Toxic Gas Detector(if applicable)
| 31 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 32 | Manufacturer | [5 empty] | will be finalized later
| 33 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. The value of End Of Line (EOL) resistor shall be suggested by vendor. 4. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 5. 3 different colors to be selected for lights of beacon: • Red for fire detection • Yellow for flammable gas detection • Blue for Toxic Gas Detector(if applicable) 6. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Horn and related beacon(Red) shall be installed on common stand. Eex JB for connectig 5*1.5 mm2 cable to be considered by vendor for signal distribution.

## BB-BR list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
BEACON LIST
ITEM | TAG NO. | LOCATION |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION | COLOR | SERVICE | REMARKS
1 | BR-2101 | Control Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified | Red | Hydrocarbon
2 | BR-2102 | Control Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified | Red | Hydrocarbon
3 | BR-2201 | Battery Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified | Red | Hydrocarbon
4 | BR-2301 | Switchgear Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified | Red | Hydrocarbon
5 | BR-2302 | Switchgear Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified | Red | Hydrocarbon
6 | BY-2201 | Battery Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified | Yellow | Hydrocarbon
7 | BY-2301 | Switchgear Building |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified | Yellow | Hydrocarbon
8
9
10
11
12 | calibration and test device for Beacons | [11 empty] | NOTE 1
1. Calibration and test devices for Beacons to be advise by vendor.

## HGD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR HYDROGEN GAS DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | Conventional
| 9 | Function | [5 empty] | Hydrogen Gas Detector
| 10 | Service | [5 empty] | See Next Page
| 11 | Sensor Type | [5 empty] | Electrochemical Type (H2S)
| 12 | Measuring Range | [5 empty] | 0 - 100% LEL
| 13 | Accuracy | [5 empty] | <+/-2 ppm
| 14 | Life Time | [5 empty] | Typical 2 to 5 Years
| 15 | Response time | [5 empty] | < 5 Seconds
| 16 | Alarm Range | [5 empty] | High Level :5% LEL , High High Level:10% LEL
| 17 | Repeatability | [5 empty] | VTA
| 18 | Output Signal | [5 empty] | Analouge 4-20mA
| 19 | Power Supply | [5 empty] | 24 VDC (VTA)
| 20 | System Wiring | [5 empty] | 2 Core x 1.5
| 21 | Power Consumption | [5 empty] | VTA (Note 8)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 24 | Installation | [5 empty] | Fix
| 25 | Mounting | [5 empty] | Bracket (Note 5)
| 26 | Mounting Accessories Material | [5 empty] | 316 SS
| 27 | Degree of Protection | [5 empty] | See Next Page
| 28 | Explosion Protection | [5 empty] | See Next Page
| 29 | Weather Proof and Dust Proof | [5 empty] | Yes
| 30 | Safety Integrity Level | [5 empty] | Non SIL
| 31 | Certificate | [5 empty] | Calibration, SIL, IEC 60529 (IP), ATEX , MATERIAL
| 32 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 33 | Manufacturer | [5 empty] | will be finalized later
| 34 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. The gas detectors shall still work after an extended period in operation ,without any low concentration of the specific gas ,none at all. 3. The response of a detector shall be clearly visible from the outside by a flashing ligh-emitting(LED) of sufficient brightness. 4. The detector shall be designed in such a way that ambient conditions, humidity, temperature and wind can not affect the sensor signal. 5. Vendor scope of supply includes: Sensor, Transmitter, All Mounting Accessories, cable glands, other accessories (including splash guard, Calibration Kit, etc) 6.Calibration kit contained CALIBRATION GAS, CALIBRATION TOOL, TEST MAGNETS (if required) shall be considered. 7. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 8. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 9. HGDs shall be capable to connect to Smart Hart Communication.
D02

## HGD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 11 از 21
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0010 | D02
HYDROGEN GAS DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | HGD-2201 | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Indoor |  | IP 54 |  | Eexd Zone1, IIC T4 |  | Hydroen (related to the batteries) | Conventional
2 | HGD-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Eexd Zone1, IIC T4 |  | Hydroen (related to the batteries) | Conventional
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20 | calibration and test device for HGDs | [12 empty] | NOTE 1
1. Calibration and test devices for HGDs to be advise by vendor.
D02
D02

## MAC
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 21
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR MANUAL ALARM CALL POINT
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Function | [5 empty] | Manual Alarm
| 9 | Service | [5 empty] | See Next Page
| 10 | Glass Type | [5 empty] | Resettable type
| 11 | Switch Type | [5 empty] | Single pole, Normally Closed و Hermetically Sealed (equipped with opening key for test, maintenance and reset)
| 12 | Detector Type | [5 empty] | Addressable
| 13 | Alarm Indicator | [5 empty] | High Intensity Red LED
| 14 | Output Signal | [5 empty] | Voltage Free Contact (24VDC,5A)
| 15 | System Wiring | [5 empty] | 2 Core
| 16 | Test Key | [5 empty] | Required
| 17 | Power Supply | [5 empty] | 24 VDC (VTA)
| 18 | Electrical Connection | [5 empty] | M20 x 1.5
| 19 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 20 | Colour | [5 empty] | Red With Black Marking Colour
| 21 | End of Line Resistor | [5 empty] | Yes
| 22 | Mounting | [5 empty] | Bracket (Note 2)
| 23 | Mounting Accessories Material | [5 empty] | 316 SS
| 24 | Degree of Protection | [5 empty] | See Next Page
| 25 | Explosion Protection | [5 empty] | Unclassified
| 26 | Safety Integrity Level | [5 empty] | Non SIL
| 27 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-11
| 28 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 29 | Manufacturer | [5 empty] | will be finalized later
| 30 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Mounting Accessories, cable gland,sunshade are included in vendor scope of supply. 3. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body.

## MAC list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 13 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
MANUAL ALARM CALL POINT LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | MAC-2101 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
2 | MAC-2102 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
3 | MAC-2103 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
4 | MAC-2104 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
5 | MAC-2201 | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
6 | MAC-2202 | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
7 | MAC-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon | Addressable
8 | MAC-2302 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
9 | MAC-2303 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
10 | MAC-2304 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon | Addressable
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28 | calibration and test device for MACs | [12 empty] | NOTE 1
1. Calibration and test devices for MACs to be advise by vendor.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02

## LHD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 14 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR LINEAR HEAT DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | Addressable
| 9 | Function | [5 empty] | Heat Detection
| 10 | Service | [5 empty] | See Next Page
| 11 | Sensor Type | [5 empty] | Two Twisted Steel Conductors with Heat Sensitive Polymer Coated
| 12 | Outer Sheath Material | [5 empty] | PVC or Chemical Resistant Nylon (VTA)
| 13 | Overall Diameter (mm) | [5 empty] | 3.5 ~ 4.5 mm (VTA)
| 14 | Alarm Temperature | [5 empty] | 85°C
| 15 | Temperature Rise | [5 empty] | 8 °C Perminute
| 16 | Cable Lentgh | [5 empty] | 15 m
| 17 | Output Signal | [5 empty] | Digital 0-24VDC
| 18 | Power Supply | [5 empty] | 24 VDC (VTA)
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Electrical Connection | [5 empty] | M20 x 1.5
| 21 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 22 | Installation | [5 empty] | Fix
| 23 | Mounting | [5 empty] | Electrical Transformer Surface Mounted
| 24 | Mounting Accessories Material | [5 empty] | VTA
| 25 | Degree of Protection | [5 empty] | See Next Page
| 26 | Explosion Protection | [5 empty] | See Next Page
| 27 | Weather Proof and Dust Proof | [5 empty] | Yes
| 28 | Safety Integrity Level | [5 empty] | Non SIL
| 29 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 30 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 31 | Manufacturer | [5 empty] | will be finalized later
| 32 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Mounting Accessories, shelter and cable gland are included in vendor scope of supply. 3. All devices shall have stainless steel tag plate with their tag no. engraved on it which is fixed on the body. 4. All required mounting & Termination accessories to be provided by vendor.

## LHD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 15 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
LINEAR HEAT DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | LHD-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
2 | LHD-2302 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
3 | LHD-2303 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
4 | LHD-2304 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
5 | LHD-2305 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Outdoor |  | IP 65 |  | Unclassified |  | Hydrocarbon
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27 | calibration and test device for LHDs | [12 empty] | NOTE 1
1. Calibration and test devices for LHDs to be advise by vendor.

## SD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 16 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR SMOKE DETECTOR/HEAT & SMOKE DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | Addressable
| 9 | Function | [5 empty] | Smoke Detector
| 10 | Service | [5 empty] | False floor / Ceiling smoke detection
| 11 | Sensor Type | [5 empty] | Smoke Sensing Element : Optical type(scattered-light type or transmitted-light type detectors)
| 12 | Rate of Rise(ROR) | [5 empty] | Yes (Temperature Rise: 8 °C Perminute )
| 13 | Built-in-Test | [5 empty] | Manual
| 14 | Area Coverage | [5 empty] | 50 m²
| 15 | Operating Temprature | [5 empty] | -10 ºC to 60 ºC
| 16 | Alarm Set point | [5 empty] | VTC
| 17 | Output Signal | [5 empty] | VTA
| 18 | Power Supply | [5 empty] | 24 VDC (VTA)
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Contact Type & Rating | [5 empty] | 24 VDC, DPDT
| 21 | Power Consumption | [5 empty] | VTA (Note 7)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 24 | Installation | [5 empty] | Fix
| 25 | Sampling Frequency | [5 empty] | VTA
| 26 | Mounting | [5 empty] | Under false floor/ Ceiling (Note 6)
| 27 | Mounting Accessories Material | [5 empty] | VTA
| 28 | Degree of Protection | [5 empty] | See Next Page
| 29 | Explosion Protection | [5 empty] | See Next Page
| 30 | Weather Proof and Dust Proof | [5 empty] | Yes
| 31 | Safety Integrity Level | [5 empty] | Non SIL
| 32 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 33 | Sensitivity Adjustable Required | [5 empty] | Yes
| 34 | Smoke detector sensitivity | [5 empty] | m = 0.11 ÷ 0.13 dB/m (pursuant to EN 14604:2005)
| 35 | Indicator | [5 empty] | 2 LED Indication for local display and also a Remote Indicator for False Ceiling / False Floor application.
| 36 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 37 | Manufacturer | [5 empty] | will be finalized later
| 38 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Detectors shall have an inherently stable operation with built in compensation being impaired by dust, dirt or humidity. 3. All circuity must be protected against electrical trasients and electromagnetic interferences. 4. Faulty zone wiring shall not damage the detector. 5. A Built in barrier shall prevent entry of insects in the sensors. 6. Mounting Accessories, cable gland, end of line resistor are included in vendor scope of supply. 7. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor. 8. Remote Indicator For False Ceiling /False Floor Smoke detector shall be considered.

## SD list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 17 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
SMOKE DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | REMARKS
1 | SD-2101 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
2 | SD-2102 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
3 | SD-2103 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
4 | SD-2104 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
5 | SD-2111 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
6 | SD-2112 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
7 | SD-2113 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
8 | SD-2114 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
9 | SD-2121 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
10 | SD-2201 | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
11 | SD-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
12 | SD-2302 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
13 | SD-2303 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
14 | SD-2311 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
15 | SD-2312 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
16 | SD-2313 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
17 | SD-2314 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
18 | SD-2315 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
19 | SD-2316 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
20 | SD-2105 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
21 | SD-2106 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
22 | SD-2122 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified
23
24
25
26
27
28
29
30
31
32
33
34
35
36 | calibration and test device for SDs | [12 empty] | NOTE 1
1. Calibration and test devices for SDs to be advise by vendor.

## BL
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 18 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN |  | DT | 0010 | D02
DATASHEET FOR BELL
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Ambient Temprature Min / Max (ºC) | [5 empty] | -5 ~ 50 (ºC)
| 3 | Design Relative Humidity Min / Max (%) | [5 empty] | 0~ 100 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic, Harsh and Dusty
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | System Type | [5 empty] | See Next Page
| 9 | Sound Pressure Level | [5 empty] | 80 dB (At 1 meter) (VTA)
| 10 | Service | [5 empty] | See Next Page
| 11 | Adjustable Sound Intensity | [5 empty] | Yes
| 12 | Adjustable Sound In Intensity | [5 empty] | Yes
| 13 | No. of Selectable Tones | [5 empty] | Minimum 2
| 14 | Power Supply | [5 empty] | 24 VDC (VTA)
| 15 | System Wiring | [5 empty] | 2 Core x 1.5
| 16 | Power Consumption | [5 empty] | VTA (Note 4)
| 17 | Electrical Connection | [5 empty] | M25 x 1.5
| 18 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 19 | Installation | [5 empty] | Fix
| 20 | Mounting | [5 empty] | Yoke (Note 2)
| 21 | Mounting Accessories Material | [5 empty] | 316 SS
| 22 | Degree of Protection | [5 empty] | See Next Page
| 23 | Explosion Protection | [5 empty] | See Next Page
| 24 | Weather Proof and Dust Proof | [5 empty] | Yes
| 25 | Safety Integrity Level | [5 empty] | Non SIL
| 26 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , BSI EN54-3
| 27 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 28 | Manufacturer | [5 empty] | will be finalized later
| 29 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Vendor shall specify weight, color and dimentions of devices and accessories. 3. Mounting Accessories, sunshade and cable gland are included in vendor scope of supply. 4. All devices shall have stainless steel tag plate with their tag no engraved on it which is fixed on the body. 5. Low power consumption to be considered. Quiescence power consumption and alarm power consumption to be specified by vendor.

## BL list
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 19 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
BELL LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  | Indoor / Outdoor |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION |  | SERVICE | REMARKS
1 | BL-2101 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon
2 | BL-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  | Indoor |  | IP 54 |  | Unclassified |  | Hydrocarbon
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19 | calibration and test device for Bells | [12 empty] | NOTE 1
1. Calibration and test devices for Bells to be advise by vendor.
D02

## HD
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 20 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
DATASHEET FOR HEAT DETECTOR
GENERAL | 1 | Tag No. | [5 empty] | See Next Page
| 2 | Recorded Ambient Temprature Min / Max (ºC) | [5 empty] | -2 ~ 52 (ºC)
| 3 | Relative Humidity @ Min recorded temp. / @ Max recorded temp. (%) | [5 empty] | 13~ 92 (%)
| 4 | Atmospheric Condition | [5 empty] | Non-Acidic
| 5 | Area Classification | [5 empty] | See Next Page
| 6 | F&G Location Layout No. | [5 empty] | See Next Page
| 7 | Location of Installation | [5 empty] | See Next Page
DETECTOR | 8 | Detector Type | [5 empty] | Addressable
| 9 | Function | [5 empty] | Heat Detector
| 10 | Service | [5 empty] | False floor / Ceiling heat detection
| 11 | Sensor Type | [5 empty] | Heat Sensing Element: Fusible Alloy Silver Contact
| 12 | Rate of Rise(ROR) | [5 empty] | Yes (Temperature Rise: 8 °C Perminute )
| 13 | Built-in-Test | [5 empty] | Manual
| 14 | Area Coverage | [5 empty] | 37 m²
| 15 | Operating Temprature | [5 empty] | -10 ºC to 90 ºC
| 16 | Alarm Set point | [5 empty] | VTC
| 17 | Output Signal | [5 empty] | VTA
| 18 | Power Supply | [5 empty] | 24 VDC (VTA)
| 19 | System Wiring | [5 empty] | 2 Core x 1.5
| 20 | Contact Type & Rating | [5 empty] | 24 VDC, DPDT
| 21 | Power Consumption | [5 empty] | VTA (Note 7)
| 22 | Electrical Connection | [5 empty] | M20 x 1.5
| 23 | Body and Housing Material | [5 empty] | Epoxy coated die cast aluminum
| 24 | Installation | [5 empty] | Fix
| 25 | Sampling Frequency | [5 empty] | VTA
| 26 | Mounting | [5 empty] | Under false floor/ Ceiling (Note 6)
| 27 | Mounting Accessories Material | [5 empty] | VTA
| 28 | Degree of Protection | [5 empty] | See Next Page
| 29 | Explosion Protection | [5 empty] | See Next Page
| 30 | Weather Proof and Dust Proof | [5 empty] | Yes
| 31 | Safety Integrity Level | [5 empty] | Non SIL
| 32 | Certificate | [5 empty] | IEC 60529 (IP), ATEX , MATERIAL
| 33 | Sensitivity Adjustable Required | [5 empty] | Yes
| 34 | Indicator | [5 empty] | 2 LED Indication for local display
| 35 | Nameplates Material | [5 empty] | Stainless Steel
PURCHASE DATA | 36 | Manufacturer | [5 empty] | will be finalized later
| 37 | Model No. | [5 empty] | will be finalized later
Notes : 1. VTA : Vendor To Advice. VTC : Vendor To Confirm N/A : Not Applicable 2. Detectors shall have an inherently stable operation with built in compensation being impaired by dust, dirt or humidity. 3. All circuity must be protected against electrical trasients and electromagnetic interferences. 4. Faulty zone wiring shall not damage the detector. 5. A Built in barrier shall prevent entry of insects in the sensors. 6. Mounting Accessories, cable gland, end of line resistor are included in vendor scope of supply. 7. Low power consumption to be considered.
D02
D02

## HD LIST
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR F&G DEVICES - EXTENSION OF BINAK BC MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 21 از 21
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 120 | IN | DT | 0010 | D02
HEAT DETECTOR LIST
ITEM | TAG NO. | LOCATION |  |  | LAYOUT |  |  |  | INDOOR / OUTDOOR |  | INGRESS PROTECTION |  | ELECTRICAL PROTECTION | REMARKS
1 | HD-2101 | Control Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (2 OF 4) |  |  |  | INDOOR |  | IP 54 |  | Unclassified
2 | HD-2201 | Battery Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (3 OF 4) |  |  |  | INDOOR |  | IP 54 |  | Eexd Zone1, IIC T4
3 | HD-2301 | Switchgear Building |  |  | BK-W007S-PEDCO-110-IN-PY-0005 (4 OF 4) |  |  |  | INDOOR |  | IP 54 |  | Eexd Zone1, IIC T4
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23 | calibration and test device for HDs | [11 empty] | NOTE 1
1. Calibration and test devices for SDs & SD/HDs to be advise by vendor.
D02