## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0008_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1856 |  |  | Transmital Date: 13 Feb 2023
Document Title: F&G Detector List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1856 |  |  | Transmital Date: 13 Feb 2023
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-LI-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | ملاحظه گردید.
2 | در صورت تغيير در هر كدام از مدارك وابسته، در اين مدرك نيز منعكس گردد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | مدرک مطابق آخرین نسخه از مدرک layout ارائه گردید.
3 | تاييد گردد كه امكان تامين H2 Detector بصورت Addressable وجود دارد؟ |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | مطابق هماهنگی با سازندگان این دتکتور از نوع ادرس پذیرموجود است اما برای تسهیل در مراحل خرید ( با توجه به محدودیت های پیش رو) ، HGD به نوع آنالوگ CONVENTIONAL-HART تغییر پیدا کرد. این مورد در سایر مدارک نیز اصلاح میگردد.
4 | Area Classification مربوط به MAC-2304 اصلاح گردد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | مدرک مطابق آخرین نسخه از مدرک layout ارائه گردید.
5 | شماره لوپ درج گردد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | اعمال گردید.
6 | مشخص گردد كه ادوات اطفا و اعلان حريق از نوع آدرس پذير مي باشد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | اعمال گردید.
7 | ديتكتورهاي سقف كاذب، remote LED درج گردد. |  | BK-SUR-ENG-INS-01-07023 | 2023-02-27 | در قالب نوت ارائه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 26 Feb 2023 |  |  |  |  | Date: