## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-PY-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1107 |  |  | Transmital Date: 22-Jun-2022
Document Title: Area Lighting & Small Power Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1107 |  |  | Transmital Date: 22-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-PY-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as IFA after finalizing or minor comments on following documents: -Calculation Note For Outdoor Area Lighting System -Plot plan Drawing -Hazardous area classification layout |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
2 | According to basic electrical design criteria, outdoor area lighting cables shall be 5 cores instead of 4 cores. So it shall be rechecked and modifid. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
3 | Tower/Flood Lighting fixture/JB technical description shall be added to legend.( Lighting fixturers outdoor installation shall be considered IP65.) |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
4 | According to lighting towers locations, it seems, it is necessary to consider lighting fixturers for following locations in order to facilitate maintenance and repair activities during operation stage. : 1) Air coolers specially under air coolers 2) Flare KO. drum/Close drain and sump pumps and related walk way and stair way 3) Suction drums platform and stair ways 4) slug pums shelter and other paltform, walk way and stair way in project (If required.) |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
5 | Typical installation detail for each lighting equipment shall be added and specified base on "Typical Installation Details & Notes For Lighting System". |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
6 | If it is necessary to consider duct bank to pass the cable through the roads, it shall be shown. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
7 | Emergency lighting shall be considered and shown in layout. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
8 | Hazardous area classification layout shall be added as reference documents. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | اعمال گردید.
9 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-05009 | 2022-07-06 | در صورت وجود هر گونه کامنت، متعاقبا اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 06-Jul-22 |  |  |  |  | Date: