## WALL THICKNESS
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
WALL THICKNESS CALCULATION REPORT
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 | [6 empty] | BK |  | SSGRL | PEDCO |  | 110 | PI | CN |  | 0001 |  | D02
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN01 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 , R.F. |  |  | 1 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | 03
SERVICE |  | Diesel Oil
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 1 | 1.152 | 0.875 | 1.317 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 1 | 1.178 | 0.875 | 1.346 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 1 | 1.229 | 0.875 | 1.405 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 1 | 1.305 | 0.875 | 1.491 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 1 | 1.406 | 0.875 | 1.607 | 3.91 | Sch 40 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 1 | 1.584 | 0.875 | 1.81 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 1 | 1.762 | 0.875 | 2.014 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 1 | 2.092 | 0.875 | 2.391 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 1 | 2.448 | 0.875 | 2.798 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 1 | 2.803 | 0.875 | 3.203 | 6.35 | Sch 20 | 10
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN04 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 , R.F. |  |  | 3 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | 03
SERVICE |  | Plant Air, Fire Water (AG)
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 3 | 3.152 | 0.875 | 3.602 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 3 | 3.178 | 0.875 | 3.632 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 3 | 3.229 | 0.875 | 3.69 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 3 | 3.305 | 0.875 | 3.777 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 3 | 3.406 | 0.875 | 3.893 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 3 | 3.584 | 0.875 | 4.096 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 3 | 3.762 | 0.875 | 4.299 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 3 | 4.092 | 0.875 | 4.677 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 3 | 4.448 | 0.875 | 5.083 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 3 | 4.803 | 0.875 | 5.489 | 6.35 | Sch 20 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.125 | 53.967 | 3 | 5.134 | 0.875 | 5.867 | 6.35 | Sch 20 | 12
14 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 14 | 355.6 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.092 | 2.337 | 2.333 | 59.267 | 3 | 5.337 | 0.875 | 6.099 | 7.92 | Sch 20 | 14
16 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 16 | 406.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.105 | 2.667 | 2.667 | 67.733 | 3 | 5.667 | 0.875 | 6.477 | 7.92 | Sch 20 | 16
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN05 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 , R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 18.2 | 03
SERVICE |  | Closed Drain, Crude Oil, Condensate, Fuel Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 3 | 3.152 | 0.875 | 3.602 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 3 | 3.178 | 0.875 | 3.632 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 3 | 3.229 | 0.875 | 3.69 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 3 | 3.305 | 0.875 | 3.777 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 3 | 3.406 | 0.875 | 3.893 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 3 | 3.584 | 0.875 | 4.096 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 3 | 3.762 | 0.875 | 4.299 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 3 | 4.092 | 0.875 | 4.677 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 3 | 4.448 | 0.875 | 5.083 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 3 | 4.803 | 0.875 | 5.489 | 6.35 | Sch 20 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.125 | 53.967 | 3 | 5.134 | 0.875 | 5.867 | 6.35 | Sch 20 | 12
14 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 14 | 355.6 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.092 | 2.337 | 2.333 | 59.267 | 3 | 5.337 | 0.875 | 6.099 | 7.92 | Sch 20 | 14
16 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 16 | 406.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.105 | 2.667 | 2.667 | 67.733 | 3 | 5.667 | 0.875 | 6.477 | 7.92 | Sch 20 | 16
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AZ00 |  | ASME B31.3 |  |  | Carbon Steel Galvanized |  |  | CL.150 , R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | 03
SERVICE |  | Instrument Air<4”, Potable Water
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 0 | 0.152 | 0.875 | 0.174 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 0 | 0.178 | 0.875 | 0.203 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 0 | 0.229 | 0.875 | 0.262 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 0 | 0.305 | 0.875 | 0.349 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 0 | 0.406 | 0.875 | 0.464 | 3.91 | Sch 40 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 0 | 0.584 | 0.875 | 0.667 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 0 | 0.762 | 0.875 | 0.871 | 6.02 | Sch 40 | 4
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AS00 |  | ASME B31.3 |  |  | Stainless Steel - 316L |  |  | CL.150, R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 15.9 | 03
SERVICE |  | Chemical
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 0.84 | 21.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.005 | 0.127 | 0.14 | 3.55 | 0 | 0.127 | 0.875 | 0.145 | 2.77 | Sch 40S | ½
¾ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.05 | 26.7 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.175 | 4.45 | 0 | 0.152 | 0.875 | 0.174 | 2.87 | Sch 40S | ¾
1 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.315 | 33.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.008 | 0.203 | 0.219 | 5.567 | 0 | 0.203 | 0.875 | 0.232 | 3.38 | Sch 40S | 1
1½ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.9 | 48.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.011 | 0.279 | 0.317 | 8.05 | 0 | 0.279 | 0.875 | 0.319 | 3.68 | Sch 40S | 1½
2 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 2.375 | 60.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.396 | 10.05 | 0 | 0.356 | 0.875 | 0.407 | 2.77 | Sch 10S | 2
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CN05 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.300 , R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 51.1 | 03
SERVICE |  | Crude Oil, Condensate
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.015 | 0.381 | 0.14 | 3.55 | 3 | 3.381 | 0.875 | 3.864 | 4.78 | Sch 160 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.019 | 0.483 | 0.175 | 4.45 | 3 | 3.483 | 0.875 | 3.981 | 5.56 | Sch 160 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.024 | 0.61 | 0.219 | 5.567 | 3 | 3.61 | 0.875 | 4.126 | 6.35 | Sch 160 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.035 | 0.889 | 0.317 | 8.05 | 3 | 3.889 | 0.875 | 4.445 | 7.14 | Sch 160 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 0.396 | 10.05 | 3 | 4.092 | 0.875 | 4.677 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.064 | 1.626 | 0.583 | 14.817 | 3 | 4.626 | 0.875 | 5.287 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.082 | 2.083 | 0.75 | 19.05 | 3 | 5.083 | 0.875 | 5.809 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.121 | 3.073 | 1.104 | 28.05 | 3 | 6.073 | 0.875 | 6.941 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.157 | 3.988 | 1.438 | 36.517 | 3 | 6.988 | 0.875 | 7.986 | 8.18 | Sch 40 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.196 | 4.978 | 1.792 | 45.5 | 3 | 7.978 | 0.875 | 9.118 | 9.27 | Sch 40 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 51.1 | 741.2 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.233 | 5.918 | 2.125 | 53.967 | 3 | 8.918 | 0.875 | 10.192 | 10.31 | Sch 40 | 12
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CS00 |  | ASME B31.3 |  |  | Stainless Steel - 316L |  |  | CL.300 , R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 13.9 | 03
SERVICE |  | Chemical
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 0.84 | 21.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.015 | 0.381 | 0.14 | 3.55 | 0 | 0.381 | 0.875 | 0.435 | 2.77 | Sch 40S | ½
¾ | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 1.05 | 26.7 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.019 | 0.483 | 0.175 | 4.45 | 0 | 0.483 | 0.875 | 0.552 | 2.87 | Sch 40S | ¾
1 | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 1.315 | 33.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.219 | 5.567 | 0 | 0.584 | 0.875 | 0.667 | 3.38 | Sch 40S | 1
1½ | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 1.9 | 48.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.034 | 0.864 | 0.317 | 8.05 | 0 | 0.864 | 0.875 | 0.987 | 3.68 | Sch 40S | 1½
2 | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 2.375 | 60.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.042 | 1.067 | 0.396 | 10.05 | 0 | 1.067 | 0.875 | 1.219 | 2.77 | Sch 10S | 2
3 | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 3.5 | 88.9 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.062 | 1.575 | 0.583 | 14.817 | 0 | 1.575 | 0.875 | 1.8 | 3.05 | Sch 10S | 3
4 | ASTM A312 Gr.TP316L | 85 | 185 | 41.4 | 600.5 | 4.5 | 114.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.08 | 2.032 | 0.75 | 19.05 | 0 | 2.032 | 0.875 | 2.322 | 3.05 | Sch 10S | 4
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FN05 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.600 , R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 102 | 03
SERVICE |  | Crude Oil
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.14 | 3.55 | 3 | 3.762 | 0.875 | 4.299 | 4.78 | Sch 160 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.038 | 0.965 | 0.175 | 4.45 | 3 | 3.965 | 0.875 | 4.531 | 5.56 | Sch 160 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.047 | 1.194 | 0.219 | 5.567 | 3 | 4.194 | 0.875 | 4.793 | 6.35 | Sch 160 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.068 | 1.727 | 0.317 | 8.05 | 3 | 4.727 | 0.875 | 5.402 | 7.14 | Sch 160 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.085 | 2.159 | 0.396 | 10.05 | 3 | 5.159 | 0.875 | 5.896 | 8.74 | Sch 160 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.126 | 3.2 | 0.583 | 14.817 | 3 | 6.2 | 0.875 | 7.086 | 7.62 | Sch 80 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.162 | 4.115 | 0.75 | 19.05 | 3 | 7.115 | 0.875 | 8.131 | 8.56 | Sch 80 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.238 | 6.045 | 1.104 | 28.05 | 3 | 9.045 | 0.875 | 10.337 | 10.97 | Sch 80 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.31 | 7.874 | 1.438 | 36.517 | 3 | 10.874 | 0.875 | 12.427 | 12.7 | Sch 80 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.386 | 9.804 | 1.792 | 45.5 | 3 | 12.804 | 0.875 | 14.633 | 15.59 | Sch 80 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 102 | 1479.4 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.458 | 11.633 | 2.125 | 53.967 | 3 | 14.633 | 0.875 | 16.723 | 17.48 | Sch 80 | 12
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Psig) (Min. / Max.) |  | Rev
AN15 |  | ASME B31.4 |  |  | Carbon Steel |  |  | CL.150 , R.F. |  |  | 3 (mm) |  |  | NACE |  |  | - |  |  | - | 85 | - | 284 | 03
SERVICE |  | Crude Oil (Burn Pit)
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Design Factor | Longitudinal Joint Factor | Temperature Derating Factor | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | F | E | T | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | 0% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.005 | 0.127 | 0.14 | 3.55 | 3 | 3.127 | 1 | 3.127 | 3.73 | Sch 80 | ½
¾ | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.006 | 0.152 | 0.175 | 4.45 | 3 | 3.152 | 1 | 3.152 | 3.91 | Sch 80 | ¾
1 | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.007 | 0.178 | 0.219 | 5.567 | 3 | 3.178 | 1 | 3.178 | 3.38 | Sch 80 | 1
1½ | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.011 | 0.279 | 0.317 | 8.05 | 3 | 3.279 | 1 | 3.279 | 3.68 | Sch 80 | 1½
2 | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.013 | 0.33 | 0.396 | 10.05 | 3 | 3.33 | 1 | 3.33 | 3.91 | Sch 40 | 2
3 | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.02 | 0.508 | 0.583 | 14.817 | 3 | 3.508 | 1 | 3.508 | 5.49 | Sch 40 | 3
4 | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.025 | 0.635 | 0.75 | 19.05 | 3 | 3.635 | 1 | 3.635 | 7.1 |  | 4
6 | API 5L Gr.B (PSL2) | 85 | 185 | 19.58 | 284 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.037 | 0.94 | 1.104 | 28.05 | 3 | 3.94 | 1 | 3.94 | 7.1 | Sch 40 | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Psig) (Min. / Max.) |  | Rev
LN15 |  | ASME B31.4 |  |  | Carbon Steel |  |  | API 3000-RTJ |  |  | 3 (mm) |  |  | NACE |  |  | - |  |  | - | 85 | - | 1035 | 03
SERVICE |  | Crude Oil
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Design Factor | Longitudinal Joint Factor | Temperature Derating Factor | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | F | E | T | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | 0% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | API 5L Gr.B (PSL2) | 85 | 185 | 71.36 | 1035 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.017 | 0.432 | 0.14 | 3.55 | 3 | 3.432 | 1 | 3.432 | 4.78 | Sch.160 | ½
¾ | API 5L Gr.B (PSL2) | 85 | 185 | 71.36 | 1035 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.022 | 0.559 | 0.175 | 4.45 | 3 | 3.559 | 1 | 3.559 | 5.56 | Sch.160 | ¾
1 | API 5L Gr.B (PSL2) | 85 | 185 | 71.36 | 1035 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.027 | 0.686 | 0.219 | 5.567 | 3 | 3.686 | 1 | 3.686 | 6.35 | Sch.160 | 1
1½ | API 5L Gr.B (PSL2) | 85 | 185 | 71.36 | 1035 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 0.72 | 1 | 1 | 0.039 | 0.991 | 0.317 | 8.05 | 3 | 3.991 | 1 | 3.991 | 7.14 | Sch.160 | 1½
2 | API 5L Gr.52 (PSL2) | 85 | 185 | 71.36 | 1035 | 2.375 | 60.3 | 66000 | 52000 | 22000 | 0.72 | 1 | 1 | 0.033 | 0.838 | 0.396 | 10.05 | 3 | 3.838 | 1 | 3.838 | 3.91 | Sch. 40 | 2
3 | API 5L Gr.52 (PSL2) | 85 | 185 | 71.36 | 1035 | 3.5 | 88.9 | 66000 | 52000 | 22000 | 0.72 | 1 | 1 | 0.048 | 1.219 | 0.583 | 14.817 | 3 | 4.219 | 1 | 4.219 | 5.49 | Sch. 40 | 3
4 | API 5L Gr.52 (PSL2) | 85 | 185 | 71.36 | 1035 | 4.5 | 114.3 | 66000 | 52000 | 22000 | 0.72 | 1 | 1 | 0.062 | 1.575 | 0.75 | 19.05 | 3 | 4.575 | 1 | 4.575 | 6.02 | Sch. 40 | 4
6 | API 5L Gr.52 (PSL2) | 85 | 185 | 71.36 | 1035 | 6.625 | 168.3 | 66000 | 52000 | 22000 | 0.72 | 1 | 1 | 0.092 | 2.337 | 1.104 | 28.05 | 3 | 5.337 | 1 | 5.337 | 7.9 | - | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Psig) (Min. / Max.) |  | Rev
LN17 |  | ASME B31.4 |  |  | Carbon Steel |  |  | API 3000-RTJ |  |  | 6 (mm) |  |  | NACE |  |  | - |  |  | - | 85 | - | 3000 | 03
SERVICE |  | Crude Oil
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Design Factor | Longitudinal Joint Factor | Temperature Derating Factor | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | F | E | T | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | 0% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | API 5L Gr.B (PSL2) | 85 | 185 | 206.84 | 3000 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.06 | 1.524 | 0.14 | 3.55 | 6 | 7.524 | 1 | 7.524 | 7.47 | Sch. XXS | ½
¾ | API 5L Gr.B (PSL2) | 85 | 185 | 206.84 | 3000 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.075 | 1.905 | 0.175 | 4.45 | 6 | 7.905 | 1 | 7.905 | 7.82 | Sch. XXS | ¾
1 | API 5L Gr.B (PSL2) | 85 | 185 | 206.84 | 3000 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.094 | 2.388 | 0.219 | 5.567 | 6 | 8.388 | 1 | 8.388 | 9.09 | Sch. XXS | 1
1½ | API 5L Gr.B (PSL2) | 85 | 185 | 206.84 | 3000 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.136 | 3.454 | 0.317 | 8.05 | 6 | 9.454 | 1 | 9.454 | 10.15 | Sch. XXS | 1½
2 | API 5L Gr.52 (PSL2) | 85 | 185 | 206.84 | 3000 | 2.375 | 60.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.114 | 2.896 | 0.396 | 10.05 | 6 | 8.896 | 1 | 8.896 | 11.07 | Sch. XXS | 2
3 | API 5L Gr.52 (PSL2) | 85 | 185 | 206.84 | 3000 | 3.5 | 88.9 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.168 | 4.267 | 0.583 | 14.817 | 6 | 10.267 | 1 | 10.267 | 11.13 | Sch. 160 | 3
4 | API 5L Gr.52 (PSL2) | 85 | 185 | 206.84 | 3000 | 4.5 | 114.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.216 | 5.486 | 0.75 | 19.05 | 6 | 11.486 | 1 | 11.486 | 13.49 | Sch. 160 | 4
6 | API 5L Gr.52 (PSL2) | 85 | 185 | 206.84 | 3000 | 6.625 | 168.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.319 | 8.103 | 1.104 | 28.05 | 6 | 14.103 | 1 | 14.103 | 14.27 | Sch. 120 | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Psig) (Min. / Max.) |  | Rev
MN17 |  | ASME B31.4 |  |  | Carbon Steel |  |  | CL.5000 - RTJ |  |  | 6 (mm) |  |  | NACE |  |  | - |  |  | - | 85 | - | 5000 | 03
SERVICE |  | Crude Oil
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Design Factor | Longitudinal Joint Factor | Temperature Derating Factor | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | F | E | T | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | 0% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | API 5L Gr.B (PSL2) | 85 | 185 | 344.737 | 5000 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.1 | 2.54 | 0.14 | 3.55 | 6 | 8.54 | 1 | 8.54 | 7.47 | Sch. XXS | ½
¾ | API 5L Gr.B (PSL2) | 85 | 185 | 344.737 | 5000 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.125 | 3.175 | 0.175 | 4.45 | 6 | 9.175 | 1 | 9.175 | 7.82 | Sch. XXS | ¾
1 | API 5L Gr.B (PSL2) | 85 | 185 | 344.737 | 5000 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.157 | 3.988 | 0.219 | 5.567 | 6 | 9.988 | 1 | 9.988 | 9.09 | Sch. XXS | 1
1½ | API 5L Gr.B (PSL2) | 85 | 185 | 344.737 | 5000 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 0.6 | 1 | 1 | 0.226 | 5.74 | 0.317 | 8.05 | 6 | 11.74 | 1 | 11.74 | 10.15 | Sch. XXS | 1½
2 | API 5L Gr.52 (PSL2) | 85 | 185 | 344.737 | 5000 | 2.375 | 60.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.19 | 4.826 | 0.396 | 10.05 | 6 | 10.826 | 1 | 10.826 | 11.07 | Sch. XXS | 2
3 | API 5L Gr.52 (PSL2) | 85 | 185 | 344.737 | 5000 | 3.5 | 88.9 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.28 | 7.112 | 0.583 | 14.817 | 6 | 13.112 | 1 | 13.112 | 15.24 | Sch. XXS | 3
4 | API 5L Gr.52 (PSL2) | 85 | 185 | 344.737 | 5000 | 4.5 | 114.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.361 | 9.169 | 0.75 | 19.05 | 6 | 15.169 | 1 | 15.169 | 17.12 | Sch. XXS | 4
6 | API 5L Gr.52 (PSL2) | 85 | 185 | 344.737 | 5000 | 6.625 | 168.3 | 66000 | 52000 | 22000 | 0.6 | 1 | 1 | 0.531 | 13.487 | 1.104 | 28.05 | 6 | 19.487 | 1 | 19.487 | 21.95 | Sch. XXS | 6
Note: Due to the unavailability of pipes with a thickness greater than the calculated min. required thickness, maximum available schedules have been selected for below 2" pipes in class MN17 and below 1" in class LN17 according to ASME B36.10