## AN01
Diesel Oil | [7 empty] | CLASS: | AN01 | C.A. : | 1 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | No | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PBE/TOE/TBE | SCH.80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M |  | Note 1
| 2" |  | 6" | BE | SCH.40 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 8" |  | 10” | BE | SCH.20 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
Nipples | 1/2" |  | 4" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A234 WPB | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 3000# | Cap |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Reducer Conc. & Ecc. |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Union |  | ASTM A105 | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 3000# | Coupling |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Elbow 45° & 90° |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Sockolet |  | ASTM A105 | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 3000# | HEX. Head Plug |  | ASTM A105 | ASME B16.11
| 2" |  | 10" | BW | same as Pipe | Cap |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 10" | BW | same as Pipe | Tee Eq & Red |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 10" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 10" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 10" | BW | same as Pipe | Weldolet |  | ASTM A105 | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 150# | Socket welded,RF, SW, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 10" | BW | same as Pipe, 150# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 10" | BW | same as Pipe, 300# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 10" | -- | 150# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 10" | -- | 300# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 10" | BW | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A105 | ASME B16.36
CLOSURES | 1/2" |  | 10" | --- | 150# | Spectacle Blind, RF, |  | ASTM A516-Gr.60 | ASME B 16.48
GASKETS | 1/2" |  | 10" | --- | 150# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
| 1/2" |  | 10" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 10" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B7 | ASME B18.2.1
| 1/2" |  | 10" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H | ASME B18.2.2
| 1/2" |  | 10" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B7 | ASME B18.2.1
| 1/2" |  | 10" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.8 | API 602
| 2" |  | 10" | FLGD | 150# | Flexible wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A216 GR. WCB,Trim No.8 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A105 ,Trim No.8 | ISO 15761
| 2" |  | 6" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A216 GR. WCB,Trim No.8 | BS 1873
| 8” |  | 10" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,GO |  |  | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body: A 105 ,Trim No.8 | ISO 15761
| 2" |  | 10" | FLGD | 150# | Swing Type |  | Body: A216 GR. WCB ,Trim No.8 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A 105, Ball:A182 Gr.316L, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 3" | FLGD | 150# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A216 GR. WCB, Ball:A182 Gr.316L, Seat: PTFE | API 6D |  | Note 2
| 4” |  | 6” | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, Lever Operated |  |  | API 6D |  | Note 2
| 8" |  | 10” | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, GO |  |  | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A105 , Screen:A182 GR. F316L
| 2” |  | 10” | FLGD | 150# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## AN04
SERVICES: Fire Water (AG) , Plant Air | [7 empty] | CLASS: | AN04 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | No | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PBE/TOE/TBE | SCH.80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M |  | Note1
| 2" |  | 2" | BE | SCH.80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 3" |  | 6" | BE | SCH.40 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 8" |  | 8” | BE | SCH.20 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
Nipples | 1/2" |  | 4" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A234 WPB | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 3000# | Cap |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Reducer Conc. & Ecc. |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Union |  | ASTM A105 | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 3000# | Coupling |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Elbow 45° & 90° |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Sockolet |  | ASTM A105 | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 3000# | HEX. Head Plug |  | ASTM A105 | ASME B16.11
| 2" |  | 8" | BW | same as Pipe | Cap |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 8" | BW | same as Pipe | Tee Eq & Red |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 8" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 8" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 8" | BW | same as Pipe | Weldolet |  | ASTM A105 | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 150# | Socket welded,RF, SW, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 8" | BW | same as Pipe, 150# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 8" | -- | 150# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 8" | -- | 300# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 8" | BW | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A105 | ASME B16.36
CLOSURES | 1/2" |  | 8" | --- | 150# | Spectacle Blind, RF |  | ASTM A516-Gr.60 | ASME B 16.48
GASKETS | 1/2" |  | 8" | --- | 150# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
| 1/2" |  | 8" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 8" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B7 | ASME B18.2.1
| 1/2" |  | 8" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H | ASME B18.2.2
| 1/2" |  | 8" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B7 | ASME B18.2.1
| 1/2" |  | 8" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
| 2" |  | 8" | FLGD | 150# | Flexible wedge,BB, OS&Y, Renewable Seat Ring, HO |  | Body: A216 GR. WCB,Trim No.12 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | ISO 15761
| 2" |  | 6" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A216 GR. WCB, Trim No.12 | BS 1873
| 8” |  | 8" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,GO |  |  | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body: A 105 ,Trim No.12 | ISO 15761
| 2" |  | 8" | FLGD | 150# | Swing Type |  | Body: A216 GR. WCB ,Trim No.12 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A 105, Ball:A182 Gr.316L, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 3" | FLGD | 150# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A216 GR. WCB, Ball:A182 Gr.316L, Seat: PTFE | API 6D |  | Note 2
| 4" |  | 6" | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, Lever Operated |  |  | API 6D |  | Note 2
| 8” |  | 8” | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, GO. |  |  | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A105 , Screen:A182 GR. F316L
| 2” |  | 8” | FLGD | 150# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.
D01
D01
D01
D01
D01
D01

## AN05
SERVICES: Crude Oil , Close Drain, Condensate, Fuel Gas | [7 empty] | CLASS: | AN05 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PBE/TOE/TBE | SCH.80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M |  | Note1
| 2" |  | 2" | BE | SCH.80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 3" |  | 6" | BE | SCH.40 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 8" |  | 16” | BE | SCH.20 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
Nipples | 1/2" |  | 4" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A234 WPB | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 3000# | Cap |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Reducer Conc. & Ecc. |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Union |  | ASTM A105 | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 3000# | Coupling |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Elbow 45° & 90° |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Sockolet |  | ASTM A105 | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 3000# | HEX. Head Plug |  | ASTM A105 | ASME B16.11
| 2" |  | 16" | BW | same as Pipe | Cap |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 16" | BW | same as Pipe | Tee Eq & Red |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 16" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 16" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 16" | BW | same as Pipe | Weldolet |  | ASTM A105 | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 150# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 16" | BW | same as Pipe, 150# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 16" | -- | 150# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 16" | -- | 300# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 16" | BW | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A105 | ASME B16.36
CLOSURES | 1/2" |  | 10" | --- | 150# | Spectacle Blind, RF |  | ASTM A516-Gr.60 | ASME B 16.48
| 10" |  | 16" | --- | 150# | Spade (Ring & Blind), RF |  | ASTM A516-Gr.60 | ASME B 16.48
GASKETS | 1/2" |  | 16" | --- | 150# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
| 1/2" |  | 16" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 16" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B7M | ASME B18.2.1
| 1/2" |  | 16" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2HM | ASME B18.2.2
| 1/2" |  | 16" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B7M | ASME B18.2.1
| 1/2" |  | 16" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2HM | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
| 2" |  | 10" | FLGD | 150# | Flexible wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A216 GR. WCB, Trim No.12 | API 600
| 12" |  | 16" | FLGD | 150# | Flexible wedge,BB, OS&Y, Renewable Seat Ring,GO |  | Body: A216 GR. WCB, Trim No.12 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | ISO 15761
| 2" |  | 6" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A216 GR. WCB,Trim No.12 | BS 1873
| 8” |  | 16" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,GO |  |  | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body: A 105 ,Trim No.12 | ISO 15761
| 2" |  | 16" | FLGD | 150# | Swing Type |  | Body: A216 GR. WCB ,Trim No.12 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A 105, Ball:A182 Gr.316L, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 3" | FLGD | 150# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A216 GR. WCB, Ball:A182 Gr.316L, Seat: PTFE | API 6D |  | Note 2
| 4” |  | 6” | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, Lever Operated |  |  | API 6D |  | Note 2
| 8" |  | 16” | FLGD | 150# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, GO |  |  | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A105 , Screen:A182 GR. F316L
| 2” |  | 16” | FLGD | 150# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## AX02
SERVICES: Potable water (UG), Fire Water (UG) | [7 empty] | CLASS: | AX02 | C.A. : | 0 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | HDPE | NACE MR0175/ISO15156: | No | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1" |  | 8" | Fusion Welding | PN 16 | A/G, UV resistance, Adhesive bonded Bell & Spigot Joint System |  | PE100 | ISO 4427/ Man. Std
FITTINGS | 1" |  | 8" | Fusion Welding/ Flanged | PN 16 | Tee Eq& Red |  | PE100 | ISO 4427/ Man. Std
| 1" |  | 8" | Fusion Welding | PN 16 | Reducer Conc. & Ecc. |  | PE100 | ISO 4427/ Man. Std
| 1" |  | 8" | Fusion Welding | PN 16 | Saddle |  | PE100 | ISO 4427/ Man. Std
| 1" |  | 8" | Fusion Welding/ Flanged | PN 16 | CAP |  | PE100 | ISO 4427/ Man. Std
| 1" |  | 8" | Fusion Welding/ Flanged | PN 16 | Elbow 45° & 90° |  | PE100 | ISO 4427/ Man. Std
FLANGES | 1" |  | 8" | Fusion Welding | PN 16 | Flange Adapter, Butt-weld Stub End |  |  | Man. Std. ,Drilling Acc. To ASME B16.5
Rings | 1" |  | 8" | --- | 150# | Backing Ring |  | A105 | Man. Std. ,Drilling Acc. To ASME B16.5
GASKETS | 1" |  | 12" | --- | 150# | Flat Ring, 1.5 mm Thick. |  | Asbestos Free | ASME B16.20
Nut & Bolt | 1" |  | 8" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B7 (Galvanized) | ASME B18.2.1
| 1" |  | 8" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H (Galvanized) | ASME B18.2.2
Rings | 1" |  | 8" | --- | 150# | Backing Ring |  | A105 | ASME B16.5
Gate Valve | 1" |  | 8" | FLGD | 150# | Solid wedge,BB, OS&Y, Renewable Seat Ring, HO |  | Body: ASTM B148 UNS C95800, Trim: Aluminum Bronze | ASME B 16.34
Globe Valve | 1" |  | 8" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,HO |  | Material: Aluminium Bronze, ASTM B148 UNS C95800 | ASME B 16.34
Gheck Valve | 1" |  | 1 1/2" | FLGD | 150# | Lift type,Piston type, Renewable Seat Ring |  | Body and Disc Material: ASTM B 148 UNS C95800, | ASME B 16.34
| 2" |  | 8" | FLGD | 150# | Swing Type
BUTTERFLY Valves | 1" |  | 8" | FLGD | 150# | Lug, FF, FLANGED END (B16.5) , Center line seat, FB, HO |  | Body and Disc Material: ASTM B 148 UNS C95800 | ASME B 16.34
STRAINER | 1" |  | 3" | FLGD | 150# | Y-Type |  | Body & cover: Aluminum Bronze ASTM B148,
| 4” |  | 8” | FLGD | 150# | T-Type
Note1 :The super pipe material shall be used for potable water services inside the building.
Note2: Branch Table will be finalized by vendor
T-Type

## AS00
SERVICES: Chemical | [7 empty] | CLASS: | AS00 | C.A. : | 0 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Stainless Steel | NACE MR0175/ISO15156: | No | Rating: | 150#
DES. (PRES.) |  | BARG |  | 13.9 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 3/4" | PBE/TOE/TBE | SCH.40S | seamless |  | ASTM A312 TP 316L | ASME B36.19 |  | Note1
| 1" |  | 1 1/2" | PE | SCH.10S | seamless |  | ASTM A312 TP 316L | ASME B36.19
| 2" |  | 2" | BE | SCH.10S | seamless |  | ASTM A312 TP 316L | ASME B36.19
Nipples | 1/2" |  | 2" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A403 GR.WP316L | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 3000# | Cap |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Reducer Conc. & Ecc. |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Union |  | ASTM A182 GR.F316L | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 3000# | Coupling |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Elbow 45° & 90° |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Sockolet |  | ASTM A182 GR.F316L | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 2000# | HEX. Head Plug |  | ASTM A182 GR.F316L | ASME B16.11
| 2" |  | 2" | BW | same as Pipe | Cap |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Tee Eq & Red |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Weldolet |  | ASTM A182 GR.F316L | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 150# | Socket welded,RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 2" |  | 2" | BW | same as Pipe, 150# | Weld Neck, RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 2" |  | 2" | BW | same as Pipe, 300# | Weld Neck, RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 1/2" |  | 2" | -- | 300# | Blind ,RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 2" |  | 2" | BW | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A182 GR.F316L | ASME B16.36
CLOSURES | 1/2" |  | 2" | --- | 150# | Spectacle Blind, RF, |  | ASTM A 240 Gr.316L | ASME B 16.48
GASKETS | 1/2" |  | 2" | --- | 150# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
| 1/2" |  | 2" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 2" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B8M | ASME B18.2.1
| 1/2" |  | 2" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -8M | ASME B18.2.2
| 1/2" |  | 2" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B8M | ASME B18.2.1
| 1/2" |  | 2" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -8M | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A182 GR. F316L ,Trim No.10 | API 602
| 2" |  | 2" | FLGD | 150# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body:A351 GR. CF3M, Trim No.10 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A182 GR. F316L ,Trim No.10 | ISO 15761
| 2" |  | 2" | FLGD | 150# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A351 GR. CF3M,Trim No.10 | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body:A182 GR. F316L ,Trim No.10 | ISO 15761
| 2" |  | 2" | FLGD | 150# | Swing Type |  | Body: A351 GR. CF3M ,Trim No.10 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body:A182 GR. F316L, Ball:A182 Gr.316L+ ST Gr6, Trim: 316+ ST Gr6, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 2" | FLGD | 150# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A351 GR. CF3M, Ball:A182 Gr.316L+ ST Gr6, Trim: 316+ ST Gr6, Seat: PTFE | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A182 GR. F316L , Screen:A182 GR. F316L
| 2" |  | 2" | FLGD | 150# | T-Type |  | Body: A351 GR. CF3M , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## AZ00
SERVICES: Instrument Air<4”, Potable Water | [7 empty] | CLASS: | AZ00 | C.A. : | 0 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel (GALVD.) note 1 | NACE MR0175/ISO15156: | No | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | NPT | SCH.80 | seamless |  | ASTM A 106-Gr.B (GALVD.) | ASME B36.10M
| 2" |  | 4" | NPT | SCH.40 | seamless |  | ASTM A 106-Gr.B (GALVD.) | ASME B36.10M
FITTINGS | 1/2" |  | 4" | THRD | 3000# | Cap |  | ASTM A105 (GALVD.) | ASME B16.11
| 1/2" |  | 4" | THRD | 3000# | Reducer Conc. & Ecc. |  | ASTM A105 (GALVD.) | ASME B16.11
| 1/2" |  | 4" | THRD | 3000# | Union |  | ASTM A105 (GALVD.) | MSS SP-83
| 1/2" |  | 4" | THRD | 3000# | Coupling |  | ASTM A105 (GALVD.) | ASME B16.11
| 1/2" |  | 4" | THRD | 3000# | Elbow 45° & 90° |  | ASTM A105 (GALVD.) | ASME B16.11
| 1/2" |  | 4" | THRD | 3000# | Plug Hex.Head |  | ASTM A105 (GALVD.) | ASME B16.11
| 1/2" |  | 4" | THRD | 3000# | Threadolet |  | ASTM A105 (GALVD.) | MSS SP-97
FLANGES | 1/2" |  | 4" | THRD | same as Pipe, 150# | Threaded, RF, SF |  | ASTM A105 (GALVD.) | ASME B16.5
| 1/2" |  | 4" | THRD | same as Pipe, 300# | Threaded, RF, SF |  | ASTM A105 (GALVD.) | ASME B16.5
| 1/2" |  | 4" | -- | 150# | Blind ,RF, SF |  | ASTM A105 (GALVD.) | ASME B16.5
| 1/2" |  | 4" | -- | 300# | Blind ,RF, SF |  | ASTM A105 (GALVD.) | ASME B16.5
| 2" |  | 4" | THRD | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A105 (GALVD.) | ASME B16.36
CLOSURES | 1/2" |  | 4" | --- | 150# | Spectacle Blind, RF, |  | ASTM A516-Gr.60 (GALVD.) | ASME B 16.48
GASKETS | 1/2" |  | 4" | --- | 150# | FLAT RING,1.5 mm Thick. |  | NON METALS, NON ASBESTOS | ASME B16.21
| 1/2" |  | 4" | --- | 300# | FLAT RING,1.5 mm Thick. |  | NON METALS, NON ASBESTOS | ASME B16.21
Nut & Bolt | 1/2" |  | 4" | --- | 150# | Studbolt, Unified threaded |  | ASTM A193-B7 (GALVD.) | ASME B18.2.1
| 1/2" |  | 4" | --- | 150# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2H (GALVD.) | ASME B18.2.2
| 1/2" |  | 4" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B7 (GALVD.) | ASME B18.2.1
Gate Valve | 1/2" |  | 1 1/2" | THRD | 150# | Solid wedge,Screwed Bonnet, Renewable Seat Ring, HO |  | Body: ASTM B148 UNS C95800, Trim: Aluminum Bronze | BS 5154
| 2" |  | 4" | FLGD | 150# | Solid wedge,BB, OS&Y, Renewable Seat Ring, HO |  | Body: ASTM B148 UNS C95800, Trim: Aluminum Bronze
Globe Valve | 1/2" |  | 1 1/2" | THRD | 150# | Solid wedge,Screwed Bonnet, Renewable Seat Ring, HO |  | Body: ASTM B148 UNS C95800, Trim: Aluminum Bronze | BS 5154
| 2" |  | 4" | FLGD | 150# | Solid wedge,BB, OS&Y, Renewable Seat Ring, HO |  | Body: ASTM B148 UNS C95800, Trim: Aluminum Bronze
Gheck Valve | 1/2" |  | 1 1/2" | THRD | 150# | Lift type,Piston type, Renewable Seat Ring |  | Body and Trim Material: ASTM B 148 UNS C95800, | BS 5154
| 2" |  | 4" | FLGD | 150# | Swing Type |  | Body and Trim Material: ASTM B 148 UNS C95800,
Ball Valve | 1/2" |  | 1 1/2" | THRD | 150# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body ,Trim & Ball Material: ASTM B 148 UNS C95800, Seat: PTFE | ISO 17292 |  | Note 3
| 2" |  | 4" | FLGD | 150# | RB , Soft Seated, Trunnion mounted, Renewable Seat Ring, Lever Operated |  | Body ,Trim & Ball Material: ASTM B 148 UNS C95800, Seat: PTFE | API 6D |  | Note 3
STRAINER | 1/2" |  | 1 1/2" | THRD | 150# | Y-Type |  | Body: B62 , Screen:A182 GR. F316L
| 2” |  | 4” | FLGD | 150# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note1 :Hot dip galvanized coatings on fabricated shall be according to ASTM A153-B OR BS 729,
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## CN05
SERVICES: Crude Oil, Condensate | [7 empty] | CLASS: | CN05 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | 300#
DES. (PRES.) |  | BARG |  | 51.1 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PBE/TOE/TBE | SCH 160 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M |  | Note1
| 2" |  | 2" | BE | SCH 80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 3" |  | 12" | BE | SCH 40 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
Nipples | 1/2" |  | 4" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A234 WPB | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 6000# | Cap |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Reducer Conc. & Ecc. |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Union |  | ASTM A105 | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 6000# | Coupling |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Elbow 45° & 90° |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Sockolet |  | ASTM A105 | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 3000# | HEX. Head Plug |  | ASTM A105 | ASME B16.11
| 2" |  | 12" | BW | same as Pipe | Cap |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Tee Eq & Red |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Weldolet |  | ASTM A105 | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 12" | BW | same as Pipe, 600# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 12" | -- | 300# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
CLOSURES | 1/2" |  | 12" | --- | 300# | Spectacle Blind, RF |  | ASTM A516-Gr.70 | ASME B 16.48
GASKETS | 1/2" |  | 12" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 12" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B7M | ASME B18.2.1
| 1/2" |  | 12" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2HM | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
| 2" |  | 12" | FLGD | 300# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A105 , Trim No.12 | ISO 15761
| 2" |  | 6" | FLGD | 300# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A216 GR. WCB , Trim No.12 | BS 1873
| 8" |  | 12" | FLGD | 300# | OS&Y,BB,Renewable Seat Ring,GO |  | Body: A216 GR. WCB, Trim No.12 | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body: A 105 ,Trim No.12 | ISO 15761
| 2" |  | 12" | FLGD | 300# | Swing Type |  | Body: A216 GR. WCB ,Trim No.12 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A 105, Ball:A182 Gr.316L+ ST Gr6, Trim: AISI 410+ ST Gr6, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 3" | FLGD | 300# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A216 GR. WCB, Ball:A182 Gr.316L+ ST Gr6, Trim: AISI 410+ ST Gr6, Seat: PTFE | API 6D |  | Note 2
| 4” |  | 4” | FLGD | 300# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, HO |  |  | API 6D |  | Note 2
| 6” |  | 12” | FLGD | 300# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, GO |  |  | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 300# | Y-Type |  | Body: A105 , Screen:A182 GR. F316L
| 2” |  | 12” | FLGD | 300# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## CS00
SERVICES: Chemical | [7 empty] | CLASS: | CS00 | C.A. : | 0 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Stainless Steel | NACE MR0175/ISO15156: | No | Rating: | 300#
DES. (PRES.) |  | BARG |  | 13.9 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 3/4" | PBE/TOE/TBE | SCH.40S | seamless |  | ASTM A312 TP 316L | ASME B36.19 |  | Note1
| 1" |  | 1 1/2" | PE | SCH.10S | seamless |  | ASTM A312 TP 316L | ASME B36.19
| 2" |  | 2" | BE | SCH.10S | seamless |  | ASTM A312 TP 316L | ASME B36.19
Nipples | 1/2" |  | 2" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A403 GR.WP316L | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 3000# | Cap |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Reducer Conc. & Ecc. |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Union |  | ASTM A182 GR.F316L | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 3000# | Coupling |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Elbow 45° & 90° |  | ASTM A182 GR.F316L | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 3000# | Sockolet |  | ASTM A182 GR.F316L | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 2000# | HEX. Head Plug |  | ASTM A182 GR.F316L | ASME B16.11
| 2" |  | 2" | BW | same as Pipe | Cap |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Tee Eq & Red |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A403 GR.WP316L | ASME B16.9
| 2" |  | 2" | BW | same as Pipe | Weldolet |  | ASTM A182 GR.F316L | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 300# | Socket welded, RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 2" |  | 2" | BW | same as Pipe, 300# | Weld Neck, RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 1/2" |  | 2" | -- | 300# | Blind ,RF, SF |  | ASTM A182 GR.F316L | ASME B16.5
| 2" |  | 2" | BW | same as Pipe, 300# | Orifice,With 2 Hole ½” NPT Female, RF |  | ASTM A182 GR.F316L | ASME B16.36
CLOSURES | 1/2" |  | 2" | --- | 300# | Spectacle Blind, RF, |  | ASTM A 240 Gr.316L | ASME B 16.48
GASKETS | 1/2" |  | 2" | --- | 300# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 2" | --- | 300# | Studbolt, Unified threaded |  | ASTM A193-B8M | ASME B18.2.1
| 1/2" |  | 2" | --- | 300# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -8M | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A182 GR. F316L ,Trim No.10 | API 602
| 2" |  | 2" | FLGD | 300# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body:A351 GR. CF3M, Trim No.10 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A182 GR. F316L ,Trim No.10 | ISO 15761
| 2" |  | 2" | FLGD | 300# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A351 GR. CF3M,Trim No.10 | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body:A182 GR. F316L ,Trim No.10 | ISO 15761
| 2" |  | 2" | FLGD | 300# | Swing Type |  | Body: A351 GR. CF3M ,Trim No.10 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body:A182 GR. F316L, Ball:A182 Gr.316L+ ST Gr6, Trim: 316+ ST Gr6, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 2" | FLGD | 300# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A351 GR. CF3M, Ball:A182 Gr.316L+ ST Gr6, Trim: 316+ ST Gr6, Seat: PTFE | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A182 GR. F316L , Screen:A182 GR. F316L
| 2" |  | 2" | FLGD | 300# | Y-Type |  | Body: A351 GR. CF3M , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## FN05
SERVICES: Crude Oil | [7 empty] | CLASS: | FN05 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | 600#
DES. (PRES.) |  | BARG |  | 102 |  |  |  | Design Code: | ASME B31.3
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PBE/TOE/TBE | SCH 160 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M |  | Note1
| 2" |  | 2" | BE | SCH 160 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
| 3" |  | 12" | BE | SCH 80 | seamless |  | ASTM A 106-Gr.B | ASME B36.10M
Nipples | 1/2" |  | 4" | PBE/PSE/BLE | same as Pipe | Swage Nipples |  | ASTM A234 WPB | MSS SP-95
FITTINGS | 1/2" |  | 1 1/2" | SW | 6000# | Cap |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Reducer Conc. & Ecc. |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Union |  | ASTM A105 | MSS SP-83
| 1/2" |  | 1 1/2" | SW | 6000# | Coupling |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Elbow 45° & 90° |  | ASTM A105 | ASME B16.11
| 1/2" |  | 1 1/2" | SW | 6000# | Sockolet |  | ASTM A105 | MSS SP-97
| 1/2" |  | 1 1/2" | THRD | 3000# | HEX. Head Plug |  | ASTM A105 | ASME B16.11
| 2" |  | 12" | BW | same as Pipe | Cap |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Tee Eq & Red |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Reducer Conc. & Ecc. |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Elbow 45° & 90° |  | ASTM A234 GR.WPB | ASME B16.9
| 2" |  | 12" | BW | same as Pipe | Weldolet |  | ASTM A105 | MSS SP-97
FLANGES | 1/2" |  | 1 1/2" | SW | 600# | Socket welded, RF, SF |  | ASTM A105 | ASME B16.5
| 2" |  | 12" | BW | same as Pipe, 600# | Weld Neck, RF, SF |  | ASTM A105 | ASME B16.5
| 1/2" |  | 12" | -- | 600# | Blind ,RF, SF |  | ASTM A105 | ASME B16.5
CLOSURES | 1/2" |  | 12" | --- | 600# | Spectacle Blind, RF |  | ASTM A516-Gr.70 | ASME B 16.48
GASKETS | 1/2" |  | 12" | --- | 600# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20
Nut & Bolt | 1/2" |  | 12" | --- | 600# | Studbolt, Unified threaded |  | ASTM A193-B7M | ASME B18.2.1
| 1/2" |  | 12" | --- | 600# | Nut, two heavy nuts for each bolt |  | ASTM A 194 -2HM | ASME B18.2.2
Gate Valve | 1/2" |  | 1 1/2" | SW/THRD | 800# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
| 2" |  | 10" | FLGD | 600# | Solid wedge,BB, OS&Y, Renewable Seat Ring,HO |  | Body: A105 ,Trim No.12 | API 602
| 12" |  | 12" | FLGD | 600# | Flexible wedge,BB, OS&Y, Renewable Seat Ring,GO |  | Body: A216 GR. WCB, Trim No.12 | API 600
Globe Valve | 1/2" |  | 1 1/2" | SW | 800# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A105 , Trim No.12 | ISO 15761
| 2" |  | 4" | FLGD | 600# | OS&Y,BB,Renewable Seat Ring,HO |  | Body: A216 GR. WCB , Trim No.12 | BS 1873
| 6" |  | 12" | FLGD | 600# | OS&Y,BB,Renewable Seat Ring,GO |  | Body: A216 GR. WCB, Trim No.12 | BS 1873
Gheck Valve | 1/2" |  | 1 1/2" | SW | 800# | Lift type,Piston type, Renewable Seat Ring |  | Body: A 105 ,Trim No.12 | ISO 15761
| 2" |  | 12" | FLGD | 600# | Swing Type |  | Body: A216 GR. WCB ,Trim No.12 | BS 1868
Ball Valve | 1/2" |  | 1 1/2" | SW | 800# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A 105, Ball:A182 Gr.316L+ ST Gr6, Trim: AISI 410+ ST Gr6, Seat: PTFE | ISO 17292 |  | Note 2
| 2" |  | 3" | FLGD | 600# | RB, Soft Seated,Floating Ball, Renewable Seat Ring, Lever Operated |  | Body: A216 GR. WCB, Ball:A182 Gr.316L+ ST Gr6, Trim: AISI 410+ ST Gr6, Seat: PTFE | API 6D |  | Note 2
| 4” |  | 12” | FLGD | 600# | RB,Soft Seated,Trunnion mounted, Renewable Seat Ring, GO |  |  | API 6D |  | Note 2
STRAINER | 1/2" |  | 1 1/2" | SW | 800# | Y-Type |  | Body: A105 , Screen:A182 GR. F316L
| 2” |  | 12” | FLGD | 600# | T-Type |  | Body: A216 , Screen:A182 GR. F316L
Note 1: Thread end will be used just for Orifice flange connections.
Note 2: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.

## AN15
SERVICES: Crude Oil (Burn Pit) | [7 empty] | CLASS: | AN15 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | 150#
DES. (PRES.) |  | BARG |  | 18.2 |  |  |  | Design Code: | ASME B31.4
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 4" |  | 4" | BE | W.Thickness: 7.1mm | seamless/ERW |  | API 5L Gr. B PSL2 | API 5L IPS-M-PI-190
FITTINGS | 4" |  | 4" | BW | 150# | SMLS, As Per Pipe Thickness |  | ASTM A234 GR.WPB | ASME B16.9 IPS-M-PI-150
FLANGES | 4" |  | 4" | BW | 150# | WN, RF, Serrated Finish, As Per Pipe Thickness |  | ASTM A105 | ASME B16.5 IPS-M-PI-150
Spectacle Blind | 4" |  | 4" | --- | 150# | Spectacle Blind, PF |  | ASTM A516-Gr.70 | ASME B 16.48
GASKETS | 4" |  | 4" | --- | 150# | Spiral Wound, 4.45 mm Thick., RF, SF |  | S.S 316 Winding/Graphite Filler, C.S. outer & S.S 316L inner ring | ASME B16.20 IPS-M-PI-150
Nut & Bolt | --- |  | --- | --- | --- | STUD BOLTS |  | ASTM A193-B7M | ASME B18.2.1
| --- |  | --- | --- | --- | HEAVY HEX NUTS |  | ASTM A 194 -2HM | ASME B18.2.2
Gate Valve | 4" |  | 4" | FE | 1500# | OS&Y, BB, BG, FE, RF, H.O. |  | Body: A216 GR. WCB, Trim AISI 316L+Stellite 6 | API 6D IPS-MPI-110
Gheck Valve | 4" |  | 4" | FLGD | 150# | SWING TYPE, FE, RF, BC |  | Body: A216 GR. WCB ,Trim AISI 316L+ Stellite 6 | API 6D BS 1868 IPS-MPI-110
Ball Valve | 4” |  | 4" | FLGD | 150# | FO, FE, RF, H.O. |  | Body: A216 GR. WCB, AISI 316L +Stellite6, | API 6D IPS-MPI-110 |  | Note 1
Note 1: Fire Safe PER API 6FA, Anti Static, and Blow-Out Proof Stem shall be considered for these valves.
D03

## LN15
SERVICES: Crude Oil | [7 empty] | CLASS: | LN15 | C.A. : | 3 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | API 3000
DES. (PRES.) |  | BARG |  | 71.4 |  |  |  | Design Code: | ASME B31.4
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PE | SCH.160 | SMLS |  | API 5L Gr. B , PSL2 | ASME B36.10M
| 2" |  | 2" | BE | SCH.40 | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
| 3" |  | 4" | BE | SCH.40 | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
| 6" |  | 6" | BE | THK 7.9 mm | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
FITTINGS | 1/2" |  | 1 1/2" | SW | 6000# | Cap, Tee, Reducer, Elbow |  | ASTM A105 | ASME B16.11 IPS-M-PI-150
| 2" |  | 6" | BW | Same as Pipe | Cap, Tee, Reducer, Elbow |  | ASTM A860 WPHY52 | API 6A MSS-SP-75
FLANGES | 1/2" |  | 1 1/2" | SW | 1500# | RTJ |  | ASTM A105 | ASME B16.5 IPS-M-PI-150
| 2" (2 1/16") |  | 6" (7 1/16") | BW | API 3000 | API 3000. Type 6B, WN, RTJ |  | API 60K | API 6A
GASKETS | 1/2" |  | 1 1/2" | --- | 1500# | RTJ, S.S. 316 |  | S.S. 316 | ASME B16.20
| 2" (2 1/16") |  | 6" (7 1/16") | --- | API 3000 | API 3000, RTJ, S.S. 316 |  | S.S. 316 | API 6A
Nut & Bolt | 1/2" |  | 6" | --- |  | HH Nuts, Thread: Class 2B |  | ASTM A 194 -2HM | ASME B18.2.2
| 1/2" |  | 6" | --- |  | Studbolt, Thread: Class 2A |  | ASTM A193-B7M | ASME B18.2.1
Gate Valve | 1/2" |  | 1 1/2" | SW | 1500# | Solid wedge,BB, OS&Y |  | Body: A105 ,Trim: AISI 316+Stellite 6 | API 602 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | BB, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A
Gheck Valve | 1/2" |  | 1 1/2" | SW | 1500# | Horizontal Piston lift |  | Body: A105 ,Trim: AISI 316L+STELLITE6 | API 602
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | BC, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K, | API 6A
Ball Valve | 1/2" |  | 1 1/2" | SW | 1500# | FB, Soft Seated,Floating Ball |  | Body: ASTM A105, Ball: AISI 316, Trim: Soft Seat-CS ENP-75 micron-PTFE | BS 5351 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | FB,RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A

## LN17
SERVICES: Crude Oil | [7 empty] | CLASS: | LN17 | C.A. : | 6 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | API 3000
DES. (PRES.) |  | BARG |  | 207 |  |  |  | Design Code: | ASME B31.4
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PE | SCH.XXS | SMLS |  | API 5L Gr. B , PSL2 | ASME B36.10M
| 2" |  | 2" | BE | SCH.XXS | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
| 3" |  | 4" | BE | SCH.160 | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
| 6" |  | 6" | BE | SCH.120 | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
FITTINGS | 1/2" |  | 1 1/2" | SW | 9000# | Cap, Tee, Reducer, Elbow |  | ASTM A105 | ASME B16.11 IPS-M-PI-150
| 2" |  | 6" | BW | Same as Pipe | Cap, Tee, Reducer, Elbow |  | ASTM A860 WPHY52 | API 6A MSS-SP-75
FLANGES | 1/2" |  | 1 1/2" | SW | 1500# | RTJ |  | ASTM A105 | ASME B16.5 IPS-M-PI-150
| 2" (2 1/16") |  | 6" (7 1/16") | BW | API 3000 | API 3000. Type 6B, WN, RTJ |  | API 60K | API 6A
GASKETS | 1/2" |  | 1 1/2" | --- | 1500# | RTJ, S.S. 316 |  | S.S. 316 | ASME B16.20
| 2" (2 1/16") |  | 6" (7 1/16") | --- | API 3000 | API 3000, RTJ, S.S. 316 |  | S.S. 316 | API 6A
Nut & Bolt | 1/2" |  | 6" | --- |  | HH Nuts, Thread: Class 2B |  | ASTM A 194 -2HM | ASME B18.2.2
| 1/2" |  | 6" | --- |  | Studbolt, Thread: Class 2A |  | ASTM A193-B7M | ASME B18.2.1
Gate Valve | 1/2" |  | 1 1/2" | SW | 1500# | Solid wedge,BB, OS&Y |  | Body: A105 ,Trim: AISI 316+Stellite 6 | API 602 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | BB, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A
Gheck Valve | 1/2" |  | 1 1/2" | SW | 1500# | Horizontal Piston lift |  | Body: A105 ,Trim: AISI 316L+STELLITE6 | API 602
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | BC, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K, | API 6A
Ball Valve | 1/2" |  | 1 1/2" | SW | 1500# | FB, Soft Seated,Floating Ball |  | Body: ASTM A105, Ball: AISI 316, Trim: Soft Seat-CS ENP-75 micron-PTFE | BS 5351 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 3000 | FB,RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A

## MN17
SERVICES: Crude Oil | [7 empty] | CLASS: | MN17 | C.A. : | 6 mm
DES. (TEMP.) |  | °C |  | 85 |  | Basic Material: | Carbon Steel | NACE MR0175/ISO15156: | Yes | Rating: | API 5000
DES. (PRES.) |  | BARG |  | 345 |  |  |  | Design Code: | ASME B31.4
ITEM | SIZES |  |  | END | SCH./ RATING | DESCRIPTION |  | MATERIAL | STANDARD |  | NOTE
| FROM |  | TO | [5 empty] | REF,
PIPES | 1/2" |  | 1 1/2" | PE | - | SMLS |  | API 5L Gr. B , PSL2 | ASME B36.10M
| 2" |  | 3" | BE | SCH.XXS | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
| 4" |  | 6" | BE | SCH.XXS | SMLS |  | API 5L Gr. X52 , PSL2 | ASME B36.10M IPS-M-PI-190
FITTINGS | 1/2" |  | 1 1/2" | SW | 9000# | Cap, Tee, Reducer, Elbow |  | ASTM A105 | ASME B16.11 IPS-M-PI-150
| 2" |  | 6" | BW | Same as Pipe | Cap, Tee, Reducer, Elbow |  | ASTM A860 WPHY52 | API 6A MSS-SP-75
FLANGES | 1/2" |  | 1 1/2" | SW | 2500# | RTJ |  | ASTM A105 | ASME B16.5 IPS-M-PI-150
| 2" (2 1/16") |  | 6" (7 1/16") | BW | API 5000 | API 5000. Type 6B, WN, RTJ |  | API 60K | API 6A
GASKETS | 1/2" |  | 1 1/2" | --- | 2500# | RTJ, S.S. 316 |  | S.S. 316 | ASME B16.20
| 2" (2 1/16") |  | 6" (7 1/16") | --- | API 5000 | API 5000, RTJ, S.S. 316 |  | S.S. 316 | API 6A
Nut & Bolt | 1/2" |  | 6" | --- |  | HH Nuts, Thread: Class 2B |  | ASTM A 194 -2HM | ASME B18.2.2
| 1/2" |  | 6" | --- |  | Studbolt, Thread: Class 2A |  | ASTM A193-B7M | ASME B18.2.1
Gate Valve | 1/2" |  | 1 1/2" | SW | 2500# | Solid wedge,BB, OS&Y |  | Body: A105 ,Trim: AISI 316+Stellite 6 | API 602 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 5000 | BB, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A
Gheck Valve | 1/2" |  | 1 1/2" | SW | 2500# | Horizontal Piston lift |  | Body: A105 ,Trim: AISI 316L+STELLITE6 | API 602
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 5000 | BC, RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K, | API 6A
Ball Valve | 1/2" |  | 1 1/2" | SW | 2500# | FB, Soft Seated,Floating Ball |  | Body: ASTM A105, Ball: AISI 316, Trim: Soft Seat-CS ENP-75 micron-PTFE | ISO 17292 IPS-MPI-110
| 2" (2 1/16") |  | 6" (7 1/16") | FLGD | API 5000 | FB,RTJ |  | Material Class EE, Body: API 60K, Trim: API 75K | API 6A
D03
D03
D03

## branches.2
PIPE CLASS: |  | AS00 / CS00
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 4 | 4 | 4 | 4 | 3
| Size | ½ | ¾ | 1 | 1½ | 2
| Legend: |  | 1. EQUAL TEE, SW |  | 2. RED. TEE, SW |  | 3. EQUAL TEE, BW
|  |  | 4.SOCKOLET |  | 5.RED. TEE, BW |  | 6. WELDOLET
Header Size (Inch)
Branch Size (Inch)

## branches.4
PIPE CLASS: |  | AZ00
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 2 | 2 | 2 | 2 | 1
| 3 | 3 | 3 | 3 | 2 | 2 | 1
| 4 | 3 | 3 | 3 | 2 | 2 | 2 | 1
| Size | ½ | ¾ | 1 | 1½ | 2 | 3 | 4
| Legend: |  | 1. EQUAL TEE,THRD |  | 2. RED. TEE, THRD
3.RED. TEE+REDUCING BUSH ,THRD
Header Size (Inch)
Branch Size (Inch)

## branches.6
PIPE CLASS: |  | LN15/LN17/MN17
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 4 | 4 | 4 | 4 | 3
| 3 | 4 | 4 | 4 | 4 | 5 | 3
| 4 | 4 | 4 | 4 | 4 | 5 | 5 | 3
| 6 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 3
| Size | ½ | ¾ | 1 | 1½ | 2 | 3 | 4 | 6
| Legend: |  | 1. EQUAL TEE, SW |  | 2. RED. TEE, SW |  | 3. EQUAL TEE, BW
|  |  | 4.SOCKOLET |  | 5.RED. TEE, BW |  | 6. WELDOLET
Header Size (Inch)
Branch Size (Inch)

## branches.8
PIPE CLASS: |  | AN04 /AN15
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 4 | 4 | 4 | 4 | 3
| 3 | 4 | 4 | 4 | 4 | 5 | 3
| 4 | 4 | 4 | 4 | 4 | 5 | 5 | 3
| 6 | 4 | 4 | 4 | 4 | 6 | 5 | 5 | 3
| 8 | 4 | 4 | 4 | 4 | 6 | 6 | 5 | 5 | 3
| Size | ½ | ¾ | 1 | 1½ | 2 | 3 | 4 | 6 | 8
| Legend: |  | 1. EQUAL TEE, SW |  | 2. RED. TEE, SW |  | 3. EQUAL TEE, BW
|  |  | 4.SOCKOLET |  | 5.RED. TEE, BW |  | 6. WELDOLET
Header Size (Inch)
Branch Size (Inch)

## branches.10
PIPE CLASS: |  | AN01
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 4 | 4 | 4 | 4 | 3
| 3 | 4 | 4 | 4 | 4 | 5 | 3
| 4 | 4 | 4 | 4 | 4 | 5 | 5 | 3
| 6 | 4 | 4 | 4 | 4 | 6 | 5 | 5 | 3
| 8 | 4 | 4 | 4 | 4 | 6 | 6 | 5 | 5 | 3
| 10 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 5 | 5 | 3
| Size | ½ | ¾ | 1 | 1½ | 2 | 3 | 4 | 6 | 8 | 10
| Legend: |  | 1. EQUAL TEE, SW |  | 2. RED. TEE, SW |  | 3. EQUAL TEE, BW
|  |  | 4.SOCKOLET |  | 5.RED. TEE, BW |  | 6. WELDOLET
Header Size (Inch)
Branch Size (Inch)

## branches.16
PIPE CLASS: |  | AN05/FN05/CN05.
| ½ | 1
| ¾ | 2 | 1
| 1 | 2 | 2 | 1
| 1½ | 2 | 2 | 2 | 1
| 2 | 4 | 4 | 4 | 4 | 3
| 3 | 4 | 4 | 4 | 4 | 5 | 3
| 4 | 4 | 4 | 4 | 4 | 5 | 5 | 3
| 6 | 4 | 4 | 4 | 4 | 6 | 5 | 5 | 3
| 8 | 4 | 4 | 4 | 4 | 6 | 6 | 5 | 5 | 3
| 10 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 5 | 5 | 3
| 12 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 6 | 5 | 5 | 3
| 14 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 3
| 16 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 3
| Size | ½ | ¾ | 1 | 1½ | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16
|  |  | Legend: |  | 1. EQUAL TEE, SW |  | 2. RED. TEE, SW |  | 3. EQUAL TEE, BW
[5 empty] | 4.SOCKOLET |  | 5.RED. TEE, BW |  | 6. WELDOLET
Header Size (Inch)
Branch Size (Inch)